## Base Reliability_DEP
DUKE N-1 AC Monitored Facility Loadings[TARA Ver 2401.1.0.0 64-bit - Thu Aug 22 17:22:17 2024]
Scenar_1 | Monitored Facility | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont ID | Base Flow (MVA) | Cont Flow (MVA) | Final DC %Loading | Final AC %Loading | Proposed Solution
ctpc34s_br1dn | 304451 GREENVILE TT 230 314574 6EVERETS 230 1 | 340/345 | 476 | 476 | WILSON230TT-WILSON115TT-230-115-#1-&BUS | 735 | 415 | 567.5 | 115.54 | 119.22 | Affected system project to reconductor Greenville - VEPCO Everetts kV Line by 12/2026
ctpc34s_br1dn | 304219 W-SHARPB 115 304223 ROCKYMT115TT 115 1 | 340 | 239 | 239 | ROCKY-MOUNT-WILSON-230KV-LINE | 359 | 118 | 243.4 | 101.11 | 101.85 | Upgrade 1200A equipment at both ends of the Rocky Mt - Wilson 115 kV Line
ctpc34s_br1dn | 304230 WILSON115ETT 115 305310 ELMCTYSOLTAP 115 1 | 340 | 239 | 239 | ROCKY-MOUNT-WILSON-230KV-LINE | 359 | 116.2 | 241.3 | 100.2 | 100.97 | Upgrade 1200A equipment at both ends of the Rocky Mt - Wilson 115 kV Line
ctpc29s_br2dn | 304035 SUTTON115 TT 115 304557 IND 304457 115 1 | 340 | 25.3 | 25.3 | Base Case | 0 | 25.2 | - | 85.16 | 99.46 | Exisiting MV capacitors at site mitigate issue
ctpc34s_hardn | 304091 RAL BRIER CR 230 304117 DURHAM230 TT 230 1 | 340 | 540 | 540 | 304124 METHOD230 TT 230 304129 OAKDALE TAP 230 1 | 911 | 404.6 | 518.4 | 93.82 | 96.01 | Reconductor Durham - Brier Creek section of Durham-RTP 230kV line. Project 24 in 2023 CTPC Report

## Base Reliability_DEC
Monitored Facility
Season | Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | Base Rating (MVA) | Contingency Rating (MVA) | Base Flow (MVA) | Contingency Flow (MVA) | Final AC % Loading | Major Component Limited | Proposed Solution
34s | STUDY | CENT230HT1 | 306004 | 6CENTRAL 230.00 | 309406 | 1CENTRL 2 1.0000 | 2 | 264 | 277 | 147.8 | 302.7 | 109.3 | Yes | Add to CTPC Plan / Central
29s | STUDY | CENT230HT1 | 306004 | 6CENTRAL 230.00 | 309406 | 1CENTRL 2 1.0000 | 2 | 264 | 277 | 139.9 | 286 | 103.3 | Yes | Add to CTPC Plan / Central
34s | LECCGM | REFUGE | 306017 | CENTRAL 100.00 | 308722 | SSPRGSTB 100.00 | 1 | 199 | 215 | 139.1 | 206.7 | 96.8 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | DRCCGM | SADLER3 | 306058 | 6SADLERY 230.00 | 309458 | 1SADLE 4 1.0000 | 4 | 520 | 534 | 325.6 | 553.4 | 103.6 | Yes | Operating Solution
29s | DRCCGM | SADLER3 | 306058 | 6SADLERY 230.00 | 309458 | 1SADLE 4 1.0000 | 4 | 520 | 534 | 321 | 548.5 | 102.7 | Yes | Operating Solution
34s | STUDYASH3VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 120 | 152 | 58.6 | 201.7 | 142.6 | Yes | Smart Relay Scheme
29s | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 120 | 152 | 54.3 | 183.2 | 125.2 | Yes | Smart Relay Scheme
3435w | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 62.1 | 208.1 | 121.7 | Yes | Smart Relay Scheme
2930w | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 58 | 191.4 | 108.6 | Yes | Smart Relay Scheme
34s | LECCGM | AB_SHADBK2_L | 306066 | TOXAWAY 100.00 | 307617 | LAUEC41 100.00 | 2 | 96 | 96 | 86.4 | 94.6 | 96.3 | Yes | DISIS 22 - Upgrade Toxaway B/W 100 kV (Lee CC-Toxaway)
34s | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 120 | 152 | 45.1 | 159.7 | 111.8 | Yes | Smart Relay Scheme
29s | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 120 | 152 | 43.3 | 152.8 | 101.7 | Yes | Smart Relay Scheme
3435w | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 157 | 181 | 47.3 | 173 | 98 | Yes | Smart Relay Scheme
34s | STUDYASH4VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 120 | 152 | 34.6 | 171.1 | 125.7 | Yes | Smart Relay Scheme
29s | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 120 | 152 | 32 | 156.4 | 110 | Yes | Smart Relay Scheme
3435w | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 39.2 | 179.1 | 108.5 | Yes | Smart Relay Scheme
2930w | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 36.8 | 165.7 | 96.5 | Yes | Smart Relay Scheme
34s | STUDYASH4VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 120 | 152 | 54.8 | 191.7 | 139.9 | Yes | Smart Relay Scheme
29s | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 120 | 152 | 50.6 | 175.3 | 122.7 | Yes | Smart Relay Scheme
3435w | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 59.3 | 199.6 | 120.2 | Yes | Smart Relay Scheme
2930w | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 55.5 | 184.8 | 107.1 | Yes | Smart Relay Scheme
34s | STUDY | PEACHVY_RB | 306096 | DUK 306096 100.00 | 308812 | BOILTAPW 100.00 | 1 | 117 | 129 | 72.8 | 124.4 | 96.9 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 91.1 | 132.6 | 104.4 | Yes | Already in CTPC Plan / Harley
2930w | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 89.3 | 129.9 | 101.2 | Yes | Already in CTPC Plan / Harley
2930w | STUDYASH7VRS | DAVIDRIVW | 306135 | DANIEL 100.00 | 306182 | N GRNVLE 100.00 | 1 | 146 | 151 | 108.5 | 153.3 | 99.5 | Yes | Already in CTPC Plan / Davidson River
2930w | STUDYASH7VRS | CAESARW-PI_P21 | 306135 | DANIEL 100.00 | 306220 | BLREC25 100.00 | 1 | 111 | 117 | 106.5 | 126.6 | 108.2 | No | Already in CTPC Plan / Davidson River
34s | STUDY | TIGER_LT6R | 306138 | E GRNVLE 100.00 | 306161 | HIGHTOWR 100.00 | 1 | 120 | 132 | 51.8 | 125.1 | 95 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 45.5 | 103.4 | 114.4 | No | Relay setting can be adjusted
2930w | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 43.4 | 98.2 | 106.2 | No | Relay setting can be adjusted
3435w | STUDY | HORSESHOE_RB | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 47.9 | 79.7 | 107.6 | No | Continue to monitor
34s | CAT1GM | OAKVALEW | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 1 | 224 | 270 | 168.3 | 290.3 | 106.4 | No | DISIS22 - Install series switchable reactors
29s | CLI5GM | OAKVALEW | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 1 | 224 | 270 | 155.9 | 269.2 | 97.8 | No | DISIS22 - Install series switchable reactors
34s | STUDY | SHADYLEE_RB | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 2 | 224 | 270 | 161.3 | 289.3 | 107.1 | No | DISIS22 - Install series switchable reactors
29s | STUDY | SHADYLEE_RB | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 2 | 224 | 270 | 152.9 | 274.6 | 100.6 | No | DISIS22 - Install series switchable reactors
3435w | STUDY | HORSESHOE_RB | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 157 | 166 | 88.1 | 160.3 | 102 | Yes | AEU (bus conductor)
34s | LECCGM | TAYLORSW | 306198 | TIGER 100.00 | 306211 | DUK 306211 100.00 | 1 | 120 | 132 | 99.4 | 128.9 | 96.7 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | LECCGM | TAYLORSB | 306198 | TIGER 100.00 | 306212 | DUK 306212 100.00 | 1 | 120 | 132 | 123.2 | 160 | 120.5 | Yes | Continue to monitor
29s | LECCGM | TAYLORSB | 306198 | TIGER 100.00 | 306212 | DUK 306212 100.00 | 1 | 120 | 132 | 118.1 | 153.9 | 114.5 | Yes | Continue to monitor
3435w | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 92.3 | 140 | 107.4 | Yes | Already in CTPC Plan / Harley
2930w | STUDYASH5VRS | HARLEYW_P21 | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 96.2 | 135.4 | 103.6 | Yes | Already in CTPC Plan / Harley
34s | LECCGM | TIGER5 | 306226 | BRDRVR16 100.00 | 306245 | CLIFSID 100.00 | 1 | 58 | 58 | 49.9 | 56 | 97 | Yes | Continue to monitor
29s | LECCGM | TIGER5 | 306226 | BRDRVR16 100.00 | 306245 | CLIFSID 100.00 | 1 | 58 | 58 | 51 | 57.1 | 95.2 | Yes | Continue to monitor
29s | OCO1GM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 383 | 422 | 374.3 | 552.1 | 131.5 | Yes | Operating Solution
34s | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 383 | 422 | 362.8 | 532.7 | 128.3 | Yes | Operating Solution
3435w | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 398.4 | 586.6 | 111.8 | Yes | Operating Solution
29s | OCO1GM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 383 | 422 | 374.3 | 552.1 | 131.5 | Yes | Operating Solution
34s | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 383 | 422 | 362.8 | 532.7 | 128.3 | Yes | Operating Solution
3435w | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 398.4 | 586.6 | 111.8 | Yes | Operating Solution
34s | LECCGM | LNDNCRKW_RCTR | 306244 | CHESNEE 100.00 | 306297 | SPARTN T 100.00 | 1 | 58 | 65 | 42.6 | 64.8 | 99.3 | Yes | Continue to monitor
29s | LECCGM | LNDNCRKW_RCTR | 306244 | CHESNEE 100.00 | 306297 | SPARTN T 100.00 | 1 | 58 | 65 | 40.8 | 63.4 | 96.6 | Yes | Continue to monitor
3435w | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 83.1 | 169.3 | 99 | Yes | Operating Solution
34s | STUDY | DEPP321AC | 306245 | CLIFSID 100.00 | 306313 | DUK 306313 100.00 | 1 | 58 | 58 | 57.3 | 64.6 | 107.7 | Yes | Continue to monitor
29s | STUDYLECCGC | BASE CASE | 306245 | CLIFSID 100.00 | 306313 | DUK 306313 100.00 | 1 | 58 | 58 | 60.2 | 60.2 | 100.4 | Yes | Continue to monitor
34s | STUDY | LAURENCLN_B_CS#_RMVC | 306247 | CLINTON TW 100.00 | 307942 | CLINTON 100.00 | Z1 | 41.6 | 41.6 | 0 | 39.7 | 95.6 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | CLFSD5_YB | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 58 | 65 | 13.8 | 74.9 | 123.1 | Yes | System reconfiguration
29s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 58 | 65 | 10.6 | 74.8 | 122.1 | Yes | System reconfiguration
3435w | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 82.7 | 167.8 | 99 | Yes | Operating Solution
29s | OCO1GM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 383 | 422 | 374.3 | 552.1 | 131.5 | Yes | Operating Solution
34s | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 383 | 422 | 362.8 | 532.7 | 128.3 | Yes | Operating Solution
3435w | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 398.4 | 586.6 | 111.8 | Yes | Operating Solution
29s | OCO1GM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 383 | 422 | 374.3 | 552.1 | 131.5 | Yes | Operating Solution
34s | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 383 | 422 | 362.8 | 532.7 | 128.3 | Yes | Operating Solution
3435w | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 398.4 | 586.6 | 111.8 | Yes | Operating Solution
3435w | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 60.8 | 124.9 | 114 | No | Revised rating is 154 MVA
34s | PBPVGM | GLENSPB | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 85 | 93 | 53.2 | 102.9 | 113.8 | No | Revised rating is 117 MVA
29s | PBPVGM | GLENSPB | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 85 | 93 | 50.3 | 96.9 | 106.1 | No | Revised rating is 117 MVA
2930w | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 57.7 | 117.4 | 105.6 | No | Revised rating is 154 MVA
34s | STUDY | PEACHVY_YB | 306269 | LAWSONFK 100.00 | 306287 | PEACH VY 100.00 | 1 | 150 | 166 | 91.9 | 187.5 | 112.9 | No | AEU (bus conductor)
29s | STUDY | PEACHVY_YB | 306269 | LAWSONFK 100.00 | 306287 | PEACH VY 100.00 | 1 | 150 | 166 | 85 | 175.3 | 104.8 | No | AEU (bus conductor)
34s | STUDY | PEACHVY_RB | 306269 | LAWSONFK 100.00 | 306287 | PEACH VY 100.00 | 2 | 150 | 166 | 91.9 | 181.9 | 110.2 | No | AEU (bus conductor)
29s | STUDY | PEACHVY_RB | 306269 | LAWSONFK 100.00 | 306287 | PEACH VY 100.00 | 2 | 150 | 166 | 85 | 168.5 | 101.4 | No | AEU (bus conductor)
29s | LECCGM | PINEWOODW | 306269 | LAWSONFK 100.00 | 306290 | PINEWOOD B 100.00 | 1 | 120 | 132 | 86.9 | 164.2 | 124.1 | Yes | Add to CTPC Plan / Pinewood
29s | LECCGM | PINEWOODB | 306269 | LAWSONFK 100.00 | 309601 | BMONT T 100.00 | 1 | 120 | 132 | 116.7 | 164 | 124 | Yes | Add to CTPC Plan / Pinewood
3435w | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 56.7 | 121.5 | 112 | No | Revised rating is 154 MVA
34s | PBPVGM | GLENSPW | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 85 | 93 | 50.6 | 95.7 | 107.4 | No | Revised rating is 117 MVA
2930w | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 53.8 | 114.9 | 104.7 | No | Revised rating is 154 MVA
29s | PBPVGM | GLENSPW | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 85 | 93 | 47.9 | 90.4 | 100.4 | No | Revised rating is 117 MVA
3435w | STUDY | PCHVYFRNWD_W | 306287 | PEACH VY 100.00 | 306320 | BOIL TAP 100.00 | Z1 | 166 | 166 | 104.4 | 158.7 | 95.3 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 119.2 | 96.1 | No | Relay setting can be adjusted
2930w | STUDY | BRB2 | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 118.7 | 95.7 | No | Relay setting can be adjusted
3435w | STUDY | PCHVYFRNWD_B | 306287 | PEACH VY 100.00 | 308812 | BOILTAPW 100.00 | Z1 | 166 | 166 | 75 | 159.7 | 96.6 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
29s | STUDYVCS1VRS | PINEWW-LF_P21 | 306290 | PINEWOOD B 100.00 | 308808 | UNA B 100.00 | 1 | 120 | 132 | 78.9 | 132.9 | 100.1 | Yes | Add to CTPC Plan / Pinewood
34s | LECCGM | LNDNCRKW_RCTR | 306297 | SPARTN T 100.00 | 307308 | DUK 307308 100.00 | 1 | 58 | 65 | 42.7 | 65.1 | 99.2 | Yes | Continue to monitor
29s | LECCGM | LNDNCRKW_RCTR | 306297 | SPARTN T 100.00 | 307308 | DUK 307308 100.00 | 1 | 58 | 65 | 41 | 63.7 | 96.6 | Yes | Continue to monitor
3435w | STUDY | PACOLET_LT2Y | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 49.9 | 111.3 | 120.9 | No | Relay setting can be adjusted
2930w | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 47.6 | 105.5 | 113 | No | Relay setting can be adjusted
34s | MCG1GM | DEPP106 | 306333 | 6NEWPORT 230.00 | 306541 | 6MORN ST 230.00 | 1 | 421 | 421 | 379.9 | 405.8 | 96.1 | Yes | Already in CTPC Plan / Sandy Ridge
2930w | STUDY | SHLB230HT4 | 306336 | 6SHELBY 230.00 | 309462 | 1SHELB 3 1.0000 | 3 | 300 | 300 | 159.7 | 313.4 | 104.5 | Yes | Add to CTPC Plan / Shelby Bank 3
29s | STUDY | SHLB230Y | 306336 | 6SHELBY 230.00 | 309462 | 1SHELB 3 1.0000 | 3 | 284 | 297 | 145.8 | 286.7 | 96.5 | Yes | Add to CTPC Plan / Shelby Bank 3
34s | CAT1GM | NEWPORT_UGBL | 306375 | GT FALL1 100.00 | 309837 | RANGERLN 100.00 | 2 | 116 | 116 | 118.1 | 137.8 | 115.5 | Yes | Operating Solution
34s | STUDY | SHELBY_YB | 306377 | HILLTOP 100.00 | 308545 | DUK 308545 100.00 | 1 | 192 | 211 | 133 | 208.4 | 99 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | ABPVGM | WHETSTONB_CS | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 117 | 117 | 59.3 | 154.8 | 137.2 | Yes | Radial - continue to monitor
3435w | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 189 | 130.9 | Yes | Radial - continue to monitor
29s | ABPVGM | WHETSTONB_CS | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 117 | 117 | 59.3 | 146.2 | 128.9 | Yes | Radial - continue to monitor
2930w | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 178 | 121.3 | Yes | Radial - continue to monitor
2930w | STUDY | CLIFFSDE2P23MB | 306389 | DUK 306389 100.00 | 306401 | SHELBY 100.00 | 1 | 126 | 132 | 59.4 | 140.2 | 106.5 | Yes | Add to CTPC Plan / Dairyhill
29s | STUDY | CLIFFSDE2P23MB | 306389 | DUK 306389 100.00 | 306401 | SHELBY 100.00 | 1 | 96 | 105 | 43.3 | 112.3 | 105.6 | Yes | Add to CTPC Plan / Dairyhill
3435w | STUDY | CLIFFSDE2P23MB | 306390 | DUK 306390 100.00 | 308793 | CLIFS2 100.00 | 1 | 126 | 132 | 35.3 | 128.8 | 96.4 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | CAT1GM | NEWPORT_UGBL | 306416 | WATEREE 100.00 | 309837 | RANGERLN 100.00 | 2 | 116 | 116 | 117.9 | 138.2 | 115 | Yes | Operating Solution
29s | STUDY | LOOKOUT_RB_NOGEN | 306430 | NLAKES R 100.00 | 306471 | LONGVIEW 100.00 | 1 | 63 | 69 | 46.1 | 76.8 | 109.5 | No | Add to CTPC Plan / Sycamore
34s | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 845 | 845 | 486.6 | 917.1 | 104.9 | Yes | Operating Solution
3435w | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 1063 | 1063 | 602.5 | 1135.2 | 103.2 | Yes | Operating Solution
34s | STUDYMAY1VRS | HICKORYW-LOO_P21 | 306453 | CLARMNTB 100.00 | 306472 | LOOKOUT 100.00 | 1 | 150 | 166 | 97.5 | 163.5 | 96.1 | Yes | AEU (bus conductor)
34s | STUDYMAY1VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 150 | 166 | 108.9 | 180.6 | 106.2 | No | Add to CTPC Plan / Beulah RAS
3435w | STUDYASH4VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 185.3 | 265.7 | 104.6 | No | Relay setting can be adjusted
2930w | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 181.9 | 263.3 | 102.4 | No | Relay setting can be adjusted
34s | STUDY | ORCHARD100Y | 306469 | LINCOLNT 100.00 | 306488 | RUEMC20 100.00 | 1 | 109 | 120 | 55.5 | 116.9 | 96.2 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDYMAY1VRS | HICKORYB-LOO_P21 | 306472 | LOOKOUT 100.00 | 306504 | CLARMNTW 100.00 | 1 | 150 | 166 | 113.5 | 170.1 | 100 | No | AEU (bus conductor)
34s | STUDYMAY1VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 150 | 166 | 115.3 | 215.7 | 126.7 | No | Add to CTPC Plan / Beulah RAS
3435w | STUDYASH4VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 127.9 | 244.6 | 115.3 | No | Add to CTPC Plan / Beulah RAS
2930w | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 120.5 | 237.7 | 111.5 | No | Add to CTPC Plan / Beulah RAS
29s | STUDY | STAMEY_RB | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 150 | 166 | 90.8 | 181.1 | 106.3 | No | Add to CTPC Plan / Beulah RAS
34s | HHPVGM | MULLWH | 306488 | RUEMC20 100.00 | 309796 | MULLB STR208100.00 | 1 | 120 | 132 | 66.1 | 138.2 | 102.5 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | STUDYASH4VRS | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 127.9 | 265.7 | 104.6 | No | Relay setting can be adjusted
2930w | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 128.9 | 263.3 | 102.4 | No | Relay setting can be adjusted
34s | STUDY | HARSB230Y | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 3 | 446 | 492 | 351.1 | 492.5 | 100.9 | No | AEU (bus conductor, wave trap)
34s | STUDY | HARSB230R | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 4 | 446 | 492 | 351.1 | 466.8 | 95.5 | No | AEU (bus conductor, wave trap)
34s | STUDY | LKWDLNGCRK_B | 306552 | BANCROFT 100.00 | 306631 | N CHARLT 100.00 | 1 | 183 | 202 | 110.9 | 204.2 | 100.4 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | LKWDOAKLWN_B | 306552 | BANCROFT 100.00 | 306695 | BUCKEYET 100.00 | 1 | 183 | 202 | 111 | 207.7 | 102 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | STUDY | WINECOFF_YB | 306566 | CHINA GR 100.00 | 306687 | WINECOFF 100.00 | 1 | 112 | 135 | 57.2 | 135.1 | 96.8 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
29s | STUDY | HARSBRG_LT4R_CS | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 112 | 135 | 35.7 | 214.3 | 158.3 | No | Already in CTPC Plan / Concord
34s | STUDYVCS1VRS | CONCRDBS-HB_P21 | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 112 | 135 | 35.6 | 147.8 | 109 | No | Already in CTPC Plan / Concord
34s | STUDY | HBURGCRABO_B_FS | 306600 | HARRISBG 100.00 | 306601 | HCKRY GR 100.00 | 1 | 112 | 132 | 96.1 | 148 | 111.5 | Yes | Already in CTPC Plan / Crab Orchard
29s | STUDY | HBURGCRABO_B_CS | 306600 | HARRISBG 100.00 | 306601 | HCKRY GR 100.00 | 1 | 112 | 132 | 87.6 | 138.9 | 103.7 | Yes | Already in CTPC Plan / Crab Orchard
34s | STUDY | HBURGCRABO_W | 306600 | HARRISBG 100.00 | 308863 | HIC GRO BL 100.00 | 1 | 112 | 132 | 82.1 | 146.9 | 110.9 | Yes | Already in CTPC Plan / Crab Orchard
29s | STUDY | HBURGCRABO_W | 306600 | HARRISBG 100.00 | 308863 | HIC GRO BL 100.00 | 1 | 112 | 132 | 74.6 | 134.3 | 100.5 | Yes | Already in CTPC Plan / Crab Orchard
34s | STUDY | WOODLWNLT5Y | 306602 | HIL S RE 100.00 | 306631 | N CHARLT 100.00 | 1 | 194 | 208 | 79.9 | 199.1 | 98.7 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | LKWDOAKLWN_W | 306611 | LAKEWOOD 100.00 | 306649 | REMOUNT 100.00 | 1 | 166 | 183 | 138.6 | 191.8 | 103.7 | Yes | Add to CTPC Plan / Lakewood
34s | STUDY | LKWDLNGCRK_B | 306611 | LAKEWOOD 100.00 | 306690 | WOODLAWN 100.00 | 1 | 150 | 166 | 91.1 | 161.1 | 95.8 | No | AEU (bus conductor)
34s | STUDY | LKWDOAKLWN_B | 306611 | LAKEWOOD 100.00 | 306695 | BUCKEYET 100.00 | 1 | 183 | 202 | 119.9 | 217.3 | 106.2 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | LAKEWOOD_YB | 306611 | LAKEWOOD 100.00 | 308754 | BANCRO B 100.00 | 1 | 183 | 202 | 123.9 | 203.9 | 99.9 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | WFRKCABRUS_W | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 1 | 120 | 132 | 88.4 | 179 | 138.5 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
29s | STUDY | WFRKCABRUS_W | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 1 | 120 | 132 | 81.5 | 164.8 | 125.6 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
34s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 2 | 120 | 132 | 88.4 | 179.2 | 138.9 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
29s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 2 | 120 | 132 | 81.5 | 165 | 126 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
34s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 3 | 143 | 165 | 89.3 | 179.1 | 113.4 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
29s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 3 | 143 | 165 | 83.2 | 165.4 | 102.9 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
29s | STUDY | HARSBRG_LT4R_CS | 306638 | DUK 306638 100.00 | 306703 | CONCORD3 100.00 | 1 | 120 | 152 | 13.5 | 182.1 | 123.3 | Yes | Already in CTPC Plan / Concord
29s | STUDY | HARSBRG_LT4R_CS | 306638 | DUK 306638 100.00 | 309611 | CONCORD4 100.00 | 1 | 120 | 152 | 13.4 | 186.3 | 123.3 | Yes | Already in CTPC Plan / Concord
34s | STUDY | WFRKCABRUS_W | 306652 | STONEWATER 100.00 | 306707 | TRIANGLT 100.00 | 1 | 264 | 305 | 218.3 | 306 | 99.9 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | SOUTHPOINTCANAL_W2 | 306664 | DUK 306664 100.00 | 306683 | DUK 306683 100.00 | 1 | 96 | 105 | 22.4 | 100.2 | 99 | Yes | Radial - continue to monitor
34s | STUDYVCS1VRS | CABARRUSB-STNW_P21 | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 120 | 132 | 40.3 | 188.2 | 150.3 | Yes | Already in CTPC Plan / Cabarrus
29s | STUDYHAR1VRS | CABARRUSB-STNW_P21 | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 120 | 132 | 41.9 | 172.9 | 135.7 | Yes | Already in CTPC Plan / Cabarrus
34s | STUDY | WFRKCABRUS_W | 306681 | WESTFORK 100.00 | 308892 | LANGTREE TAP100.00 | 4 | 143 | 165 | 89.7 | 179.4 | 113.3 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
29s | STUDY | WFRKCABRUS_W | 306681 | WESTFORK 100.00 | 308892 | LANGTREE TAP100.00 | 4 | 143 | 165 | 83.6 | 165.6 | 102.8 | Yes | Add to CTPC Plan / Timber/Sherrill RAS
34s | ALL1GM | CANALB_FS | 306684 | DUK 306684 100.00 | 309941 | DUK 309941 100.00 | 1 | 96 | 105 | 78.4 | 100.2 | 98 | Yes | Radial - continue to monitor
3435w | BEL1GM | HORSEGAPB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 2 | 553 | 639 | 316.4 | 608.4 | 95.7 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDYHAR1VRS | DEEPRVRB-GB_P21 | 306726 | BECKRDIT 100.00 | 306805 | TRIAD PK 100.00 | 1 | 120 | 132 | 60.1 | 129.9 | 102.6 | Yes | Add to CTPC Plan / Oak Hollow
34s | STUDYHAR1VRS | DEEPRVRW-GB_P21 | 306726 | BECKRDIT 100.00 | 308922 | TRIADPK WH 100.00 | 1 | 120 | 132 | 57.8 | 125.9 | 97.2 | Yes | Add to CTPC Plan / Oak Hollow
34s | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 224 | 255 | 140 | 303.5 | 113.6 | No | AEU (bus, switch)
29s | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 224 | 255 | 131.9 | 287.2 | 107.2 | No | AEU (bus, switch)
3435w | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 150.9 | 331.1 | 98.2 | No | AEU (bus, switch)
34s | STUDY | BECKRDT_LT1R | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z2 | 224 | 255 | 140 | 297.5 | 111.2 | No | AEU (bus, switch)
29s | STUDY | BECKRDT_LT1R | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z2 | 224 | 255 | 131.9 | 280.2 | 104.1 | No | AEU (bus, switch)
3435w | STUDY | BECKRDT_LT1R | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z2 | 292 | 319 | 150.9 | 322.6 | 96.4 | No | AEU (bus, switch)
34s | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 166 | 213 | 123.9 | 219.1 | 99.5 | Yes | Add to CTPC Plan / Bethania + Shattalon
29s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 1 | 96 | 105 | 46.1 | 119.5 | 109.6 | Yes | Already in Plan / Reidsville / Wolf Creek
34s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 1 | 96 | 105 | 44.9 | 118.4 | 107.9 | Yes | Already in Plan / Reidsville / Wolf Creek
29s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 2 | 96 | 105 | 46.1 | 116.3 | 106.6 | Yes | Already in Plan / Reidsville / Wolf Creek
34s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 2 | 96 | 105 | 44.9 | 114.9 | 104.8 | Yes | Already in Plan / Reidsville / Wolf Creek
29s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 3 | 96 | 105 | 46 | 119.2 | 109.3 | Yes | Already in Plan / Reidsville / Wolf Creek
34s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 3 | 96 | 105 | 44.8 | 118.1 | 107.7 | Yes | Already in Plan / Reidsville / Wolf Creek
29s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 4 | 96 | 105 | 46 | 116 | 106.4 | Yes | Already in Plan / Reidsville / Wolf Creek
34s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 4 | 96 | 105 | 44.8 | 114.6 | 104.5 | Yes | Already in Plan / Reidsville / Wolf Creek
29s | STUDY | DANRIVS_RB | 306737 | DAN RIV 100.00 | 306810 | WENTWRTH 100.00 | 1 | 96 | 105 | 81.1 | 103.8 | 95.2 | Yes | Already in Plan / Dan River
34s | STUDY | SADLER_YB | 306737 | DAN RIV 100.00 | 306810 | WENTWRTH 100.00 | 1 | 96 | 105 | 83 | 104.4 | 95.2 | Yes | Already in Plan / Dan River
34s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 308923 | WENTW BL 100.00 | 1 | 96 | 105 | 75.7 | 109.6 | 100 | Yes | Already in Plan / Dan River
29s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 308923 | WENTW BL 100.00 | 1 | 96 | 105 | 74.5 | 107.5 | 98.6 | Yes | Already in Plan / Dan River
34s | BEL1GM | BANNERTOWNB | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 85 | 93 | 81.6 | 107 | 111.7 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | STUDY | RURLHLL_LT3R | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 111 | 117 | 76.1 | 114.1 | 99.2 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | BEL1GM | BANNERTOWNW | 306763 | MITCHL R 100.00 | 308027 | WH PLAIN 100.00 | 1 | 85 | 93 | 65.1 | 92 | 96.1 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDYHAR1VRS | DEEPRVRB-GB_P21 | 306805 | TRIAD PK 100.00 | 306986 | HP CITY5 100.00 | 1 | 120 | 132 | 59.7 | 127.8 | 102.7 | Yes | Add to CTPC Plan / Oak Hollow
3435w | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 47.3 | 171 | 107.7 | No | Revised rating is 219 MVA
2930w | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 39.9 | 155 | 95.8 | No | Revised rating is 219 MVA
34s | STUDY | PLGARDEN_RB | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 112 | 132 | 14.3 | 146.7 | 117.4 | Yes | Required Customer upgrade addresses issue
29s | STUDY | PLGARDEN_RB | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 112 | 132 | 13.2 | 141.7 | 111.9 | Yes | Required Customer upgrade addresses issue
3435w | STUDY | PLGARDN_LT3R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 14.2 | 152.3 | 102.6 | No | Required Customer upgrade addresses issue
2930w | STUDY | PLGARDN_LT2R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 14.6 | 147.2 | 97.8 | No | Required Customer upgrade addresses issue
34s | STUDYHAR1VRS | DELTAB-PARK_P21 | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 120 | 152 | 94.5 | 155.1 | 104.6 | Yes | Add to CTPC Plan / Ashe St
29s | STUDYHAR1VRS | PARKWOOD_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 120 | 152 | 89.8 | 153.3 | 102.2 | Yes | Add to CTPC Plan / Ashe St
34s | STUDY | ENO_RB | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 1 | 216 | 224 | 111.3 | 221.8 | 98.3 | No | Add to CTPC Plan / Crest St
34s | STUDY | ENO_YB | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 2 | 197 | 197 | 111.3 | 220 | 109.8 | Yes | Add to CTPC Plan / Crest St
29s | STUDY | ENO_YB | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 2 | 197 | 197 | 102.6 | 200.2 | 99.9 | Yes | Add to CTPC Plan / Crest St
34s | STUDY | ASHSTDELTA_W | 306880 | ELLIS RD_B 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 117 | 129 | 52.2 | 145 | 117.6 | Yes | Add to CTPC Plan / Delta
29s | STUDY | ASHSTDELTA_W | 306880 | ELLIS RD_B 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 117 | 129 | 56.2 | 143.8 | 115.8 | Yes | Add to CTPC Plan / Delta
34s | STUDY | ENOBRAGTWN_W | 306881 | ENO 100.00 | 306916 | HORTON R 100.00 | 1 | 109 | 120 | 64.6 | 127.1 | 103.5 | No | AEU (bus conductor)
34s | STUDY | ENO_RB | 306881 | ENO 100.00 | 308630 | HORTON TW 100.00 | 1 | 109 | 120 | 78.5 | 127.6 | 105 | No | AEU (bus conductor)
29s | STUDY | ENO_RB | 306881 | ENO 100.00 | 308630 | HORTON TW 100.00 | 1 | 109 | 120 | 72.5 | 118 | 96.2 | No | AEU (bus conductor)
34s | STUDYHAR1VRS | DEEPRVRW-BEC_P21 | 306890 | FRNDSHPT 100.00 | 306902 | GREENSBR 100.00 | 1 | 120 | 132 | 66.9 | 125.5 | 95.7 | Yes | Add to CTPC Plan / Oak Hollow
34s | SDPVGM | GRNSBOROB | 306902 | GREENSBR 100.00 | 306939 | MERIT DR 100.00 | 1 | 183 | 234 | 134.8 | 225.9 | 95.7 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | BUCCGM | DEEPRVRW | 306902 | GREENSBR 100.00 | 308930 | FRIEND B 100.00 | 1 | 120 | 132 | 73.2 | 146.2 | 112.7 | Yes | Add to CTPC Plan / Oak Hollow
29s | BUCCGM | DEEPRVRW | 306902 | GREENSBR 100.00 | 308930 | FRIEND B 100.00 | 1 | 120 | 132 | 66.4 | 134.4 | 102.6 | Yes | Add to CTPC Plan / Oak Hollow
34s | STUDY | NGBORODANR_W_RMVCAP | 306928 | JESUPTWN 100.00 | 306943 | N GREENS 100.00 | 1 | 166 | 183 | 126.6 | 178.3 | 98.9 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | PLGDNGLRVN_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 112 | 132 | 11.8 | 128.8 | 101.4 | Yes | Required Customer upgrade addresses issue
29s | STUDY | PLGDNGLRVN_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 112 | 132 | 13.5 | 125.4 | 97.6 | Yes | Required Customer upgrade addresses issue
34s | STUDY | NGBOROLKJNT_B | 306943 | N GREENS 100.00 | 308957 | JESUPT WH 100.00 | 1 | 166 | 183 | 96.9 | 182.8 | 98.9 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | ASHSTDELTA_W | 306948 | PARKWOOD 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 216 | 224 | 144.5 | 240.1 | 110 | No | AEU (switch)
29s | STUDY | ASHSTDELTA_W | 306948 | PARKWOOD 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 216 | 224 | 141.7 | 231.8 | 105.5 | No | AEU (switch)
34s | STUDY | ENO_LT2R | 306948 | PARKWOOD 100.00 | 306970 | HOPVLYTB 100.00 | 1 | 216 | 224 | 107.8 | 250.9 | 115.8 | No | AEU (switch)
29s | STUDY | ENO_LT2R | 306948 | PARKWOOD 100.00 | 306970 | HOPVLYTB 100.00 | 1 | 216 | 224 | 103.4 | 231 | 105 | No | AEU (switch)
34s | STUDY | ASHSTDELTA_B | 306948 | PARKWOOD 100.00 | 308940 | R TRNGLE_W 100.00 | 1 | 216 | 224 | 84.3 | 212 | 95.5 | No | Add to CTPC Plan / Delta
34s | STUDY | PARKWD_LT1Y | 306948 | PARKWOOD 100.00 | 309560 | PARK2 100.00 | Z1 | 216 | 224 | 101.1 | 225.7 | 100.7 | No | Revised rating is 327 MVA
34s | STUDY | PARKWD_LT1R | 306948 | PARKWOOD 100.00 | 309560 | PARK2 100.00 | Z2 | 216 | 224 | 101.1 | 216.8 | 96.6 | No | Revised rating is 327 MVA
34s | STUDY | LNDNRNDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 166 | 183 | 141.8 | 256.2 | 139.3 | Yes | Required Customer upgrade addresses issue
29s | STUDY | LNDNRNDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 166 | 183 | 132.5 | 240.5 | 131.7 | Yes | Required Customer upgrade addresses issue
3435w | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 145.8 | 267.3 | 129.7 | No | Required Customer upgrade addresses issue
2930w | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 140 | 257.5 | 124.1 | No | Required Customer upgrade addresses issue
34s | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 166 | 183 | 131.4 | 255.9 | 138.9 | Yes | Required Customer upgrade addresses issue
29s | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 166 | 183 | 119.6 | 237.2 | 129.4 | Yes | Required Customer upgrade addresses issue
3435w | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 133.1 | 259.6 | 127.2 | No | Required Customer upgrade addresses issue
2930w | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 128.1 | 250.7 | 121.9 | No | Required Customer upgrade addresses issue
34s | STUDY | EDURHAM_YB | 306967 | TREYBURN TB 100.00 | 309848 | E DURHAM RED100.00 | 1 | 96 | 105 | 67.7 | 106 | 104.3 | Yes | Radial - continue to monitor
29s | STUDY | EDURHAM_YB | 306967 | TREYBURN TB 100.00 | 309848 | E DURHAM RED100.00 | 1 | 96 | 105 | 64 | 99.4 | 97.3 | Yes | Radial - continue to monitor
34s | STUDY | ASHSTDELTA_W | 306975 | WEAVERT 100.00 | 308786 | STALLTAP 100.00 | 1 | 120 | 152 | 76.6 | 146.7 | 97.1 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | BECKERDIT_RB | 306989 | TARRANTR 100.00 | 308930 | FRIEND B 100.00 | 1 | 120 | 132 | 67.9 | 128.1 | 100.3 | Yes | Add to CTPC Plan / Oak Hollow
34s | STUDYVCS1VRS | CHEROKEW-CLI_P21 | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 58 | 65 | 13.8 | 71.1 | 124.3 | Yes | Operating Solution
29s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 58 | 65 | 10.2 | 71.1 | 123.4 | Yes | Operating Solution
34s | LECCGM | AB_SHADBK2_S | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 85 | 43.6 | 90 | 105.9 | Yes | Continue to monitor
29s | LECCGM | AB_SHADBK2_S | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 85 | 41.5 | 85.5 | 100.6 | Yes | Continue to monitor
34s | LECCGM | SHADYG1 | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 84 | 44.6 | 89.9 | 107.1 | Yes | Continue to monitor
29s | LECCGM | AB_SHADBK1_S | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 84 | 42.5 | 85.5 | 101.8 | Yes | Continue to monitor
34s | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 27.5 | 90.2 | 150.4 | Yes | Add to CTPC Plan / Tiger
3435w | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.4 | 85.4 | 142.3 | Yes | Add to CTPC Plan / Tiger
29s | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.7 | 84.2 | 140.4 | Yes | Add to CTPC Plan / Tiger
2930w | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 23.7 | 79.2 | 131.9 | Yes | Add to CTPC Plan / Tiger
34s | LECCGM | AB_SHADBK2_L | 307617 | LAUEC41 100.00 | 308622 | LEE CC 100.00 | 2 | 96 | 96 | 84.3 | 91.9 | 96.1 | Yes | DISIS 22 - Upgrade Toxaway
3435w | CLI5GM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 20.4 | 60.6 | 108.3 | Yes | Add to CTPC Plan / Shelby
2930w | WYLIGM | SHELBY2 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 25.4 | 56.7 | 101.2 | Yes | Add to CTPC Plan / Shelby
34s | AAPVGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 18.2 | 54.3 | 97 | Yes | Add to CTPC Plan / Shelby
3435w | STUDY | LAURENRAB_B_CS#_TGLC | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 41.6 | 21.7 | 40.2 | 98.2 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | STUDY | LAURENS_YB_CS#_RMVCA | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 41.6 | 22.1 | 39.9 | 96.3 | No | Identified in 10-year cases but not 5-year cases. Continue to monitor.
3435w | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 50 | 91.6 | 109 | Yes | Operating Solution
2930w | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 46.7 | 85.4 | 101.7 | Yes | Operating Solution
3435w | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 47.9 | 90.9 | 119.6 | Yes | Operating Solution
2930w | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 44.6 | 84.8 | 111.5 | Yes | Operating Solution
34s | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 39.8 | 75.4 | 99.3 | Yes | Operating Solution
34s | BUCCGM | BASE CASE | 308104 | DEERFLDR 100.00 | 308455 | NESBITBRAWL 100.00 | 1 | 143 | 143 | 141.6 | 141.6 | 100.9 | Yes | Radial - continue to monitor
3435w | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 42.6 | 89.6 | 105.5 | Yes | Operating Solution
2930w | BEL1GM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 39.9 | 83.9 | 98.8 | Yes | Operating Solution
3435w | STUDYHAR1VRS | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.9 | 47.8 | 119.6 | Yes | Operating Solution
2930w | STUDY | ENO230HT1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 15.8 | 44.5 | 111.4 | Yes | Operating Solution
34s | STUDY | ENO_LT1R | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 13.9 | 42.6 | 106.6 | Yes | Operating Solution
29s | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 12.9 | 39.3 | 98.2 | Yes | Operating Solution
3435w | THALGM | TUCKASEEBK3 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 217.5 | 398.2 | 103.2 | No | Relay setting can be adjusted
3435w | THALGM | TUCKASEEBK2 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 3 | 386 | 386 | 216.2 | 397.8 | 103.1 | No | Relay setting can be adjusted
34s | HHPVGM | MULLBL | 308589 | ORCHARD 100.00 | 308833 | RUTH20WH 100.00 | 1 | 120 | 132 | 97.6 | 138.2 | 102.5 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | HHPVGM | MULLWH | 308589 | ORCHARD 100.00 | 309796 | MULLB STR208100.00 | 1 | 120 | 132 | 66.4 | 139.5 | 102.4 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | LECCGM | AB_SHADBK2_L | 308622 | LEE CC 100.00 | 309811 | FVCRCLSPV 100.00 | 1 | 96 | 96 | 118 | 125.7 | 130 | Yes | DISIS 22 - Upgrade Toxaway B/W 100 kV (Lee CC-Toxaway)
34s | STUDY | PARKWD_LT3R | 308631 | DUK 308631 100.00 | 308994 | DUK 308994 100.00 | 1 | 117 | 129 | 23.9 | 121.5 | 100.7 | Yes | Identified in 10-year cases but not 5-year cases. Continue to monitor.
34s | CAT1GM | BELMONTW | 308729 | ALLENCT2 100.00 | 308865 | LTLROKTO 100.00 | 1 | 109 | 120 | 67.2 | 119.3 | 102.4 | No | Radial - continue to monitor
34s | STUDYMAY1VRS | PERRYB-LEE_P21 | 308762 | DUK 308762 100.00 | 308763 | MOONVI W 100.00 | 1 | 109 | 120 | 68.8 | 119.4 | 99.1 | No | DISIS22 - AEU
34s | STUDY | ASHSTDELTA_W | 308786 | STALLTAP 100.00 | 309848 | E DURHAM RED100.00 | Z1 | 193 | 193 | 116.1 | 187.5 | 96.9 | No | Already in CTPC Plan / Panther
34s | STUDYVCS1VRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 58 | 65 | 14.1 | 72.5 | 123.3 | Yes | Operating Solution
29s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 58 | 65 | 10.5 | 72.4 | 122.4 | Yes | Operating Solution
34s | STUDY | CLFSD5_YB | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 58 | 65 | 13.8 | 73.3 | 123.3 | Yes | System reconfiguration
29s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 58 | 65 | 10.5 | 73.3 | 122.3 | Yes | System reconfiguration
29s | LECCGM | PINEWOODB | 308802 | PINEWOOD W 100.00 | 309601 | BMONT T 100.00 | 1 | 120 | 132 | 116.7 | 164 | 124 | Yes | Add to CTPC Plan / Pinewood
34s | STUDYVCS1VRS | CHEROKEW-CLI_P21 | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 58 | 65 | 14.1 | 71.8 | 124.2 | Yes | Operating Solution
29s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 58 | 65 | 10.5 | 71.8 | 123.3 | Yes | Operating Solution
34s | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 308940 | R TRNGLE_W 100.00 | 1 | 117 | 129 | 83.7 | 156.8 | 124.8 | Yes | Add to CTPC Plan / Delta
29s | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 308940 | R TRNGLE_W 100.00 | 1 | 117 | 129 | 82.9 | 152.2 | 119.7 | Yes | Add to CTPC Plan / Delta
3435w | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 260.7 | 436.6 | 105.2 | No | AEU (CT)
34s | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 261.2 | 436.2 | 105.1 | No | AEU (CT)
2930w | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 247.6 | 414.5 | 99.9 | No | AEU (CT)
29s | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 247.7 | 413.8 | 99.7 | No | AEU (CT)
34s | STUDY | CENT230HT1 | 309406 | 1CENTRL 2 1.0000 | 309502 | CENT2 100.00 | 2 | 259 | 268 | 146.1 | 294.5 | 109.9 | No | Add to CTPC Plan / Central
29s | STUDY | CENT230HT1 | 309406 | 1CENTRL 2 1.0000 | 309502 | CENT2 100.00 | 2 | 259 | 268 | 138.4 | 279.3 | 104.2 | No | Add to CTPC Plan / Central
3435w | LECCGM | PISGAH2 | 309450 | 1PISGA 1 1.0000 | 309513 | PISG1 100.00 | 1 | 220 | 246 | 154.6 | 233.9 | 95.1 | No | AEU (CT)
3435w | CLI5GM | PISGAH1 | 309451 | 1PISGA 2 1.0000 | 309514 | PISG2 100.00 | 2 | 246 | 246 | 157.6 | 236.2 | 96 | No | AEU (CT)
34s | DRCCGM | SADLER3 | 309458 | 1SADLE 4 1.0000 | 309518 | SADL4 100.00 | 4 | 520 | 534 | 325.6 | 553.4 | 103.6 | Yes | Operating Solution
29s | DRCCGM | SADLER3 | 309458 | 1SADLE 4 1.0000 | 309518 | SADL4 100.00 | 4 | 520 | 534 | 321 | 548.5 | 102.7 | Yes | Operating Solution
29s | STUDY | SHLB230Y | 309462 | 1SHELB 3 1.0000 | 309543 | SHE3 100.00 | 3 | 246 | 268 | 143.5 | 276.9 | 103.3 | No | Add to CTPC Plan / Shelby
2930w | STUDY | SHLB230Y | 309462 | 1SHELB 3 1.0000 | 309543 | SHE3 100.00 | 3 | 300 | 300 | 157.2 | 301.7 | 100.6 | Yes | Add to CTPC Plan / Shelby
34s | STUDYLE78GC | LEESREDYRV_W# | 306041 | LEE 100.00 | 308492 | PERRYT B 100.00 | 1 | 224 | 270 | 201 | 294.9 | 110.3 | No | DISIS22 - AEU (switch)
29s | STUDY | LEESREDYRV_W#_NOGEN | 306041 | LEE 100.00 | 308492 | PERRYT B 100.00 | 1 | 224 | 270 | 192 | 273.5 | 101.5 | No | DISIS22 - AEU (switch)
29s | STUDY | LEESREDYRV_W#_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 484 | 519 | 290.3 | 801.7 | 148.4 | No | Add to CTPC Plan / States
2930w | STUDY | LEESREDYRV_W#_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 519 | 519 | 290.5 | 795.3 | 147.1 | No | Add to CTPC Plan / States
34s | STUDYASH7VRS | WESTMINB-CE_P21 | 306063 | SENCA TW 100.00 | 306081 | BLREC26 100.00 | 1 | 197 | 218 | 93 | 217.4 | 103.5 | No | Smart Relay Scheme
34s | STUDYMAY1VRS | PERRYB-LEE_P21 | 306103 | DUK 306103 100.00 | 308762 | DUK 308762 100.00 | 1 | 109 | 120 | 68.7 | 119.1 | 99.1 | No | DISIS22 - AEU
3435w | THALGM | SHULERB | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 216.9 | 383.9 | 98.1 | No | Relay setting can be adjusted
3435w | THALGM | SHULERW | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 1 | 386 | 386 | 216.9 | 383.9 | 98.1 | No | Relay setting can be adjusted
3435w | STUDY | HORSESHOE_RB | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 24.2 | 129.7 | 107.3 | No | AEU (bus conductor)
2930w | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 19 | 121 | 95.7 | No | AEU (bus conductor)
3435w | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 48.4 | 86.8 | 110.3 | No | Continue to monitor
2930w | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 41.6 | 76.6 | 95.2 | No | Continue to monitor
3435w | STUDY | HORSESHOE_RB | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 52 | 89.1 | 110.6 | No | Continue to monitor
2930w | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 44.6 | 79.9 | 96.9 | No | Continue to monitor

## Local Economic_DEP
DUKE N-1 AC Monitored Facility Loadings[TARA Ver 2401.1.0.0 64-bit - Tue Aug 27 11:56:24 2024]
Scenar_1 | Monitored Facility | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont ID | Base Flow (MVA) | Cont Flow (MVA) | Final DC %Loading | Final AC %Loading | Proposed Solution
ctpc34w-DUK-CPLE_rob2dn | 304696 SHAW AFB TAP 115 370238 3EASTOVER! 115 1 | 340/343 | 135 | 141 | SUMTER-SCE&G-WATEREE-PLANT-230KV-LINE | 192 | 78 | 138.4 | 99.17 | 98.15 | Reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F. Project 120 in 2023 CTPC Report
ctpc34w-SOCO-DUK_rob2dn | 304696 SHAW AFB TAP 115 370238 3EASTOVER! 115 1 | 340/343 | 135 | 141 | SUMTER-SCE&G-WATEREE-PLANT-230KV-LINE | 200 | 77.6 | 137.6 | 98.66 | 97.61 | Reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F. Project 120 in 2023 CTPC Report
ctpc34w-DUK-CPLE_hardn | 304323 RAMSEUR TAP 115 304331 ASHEBO115WTT 115 1 | 340 | 229 | 229 | 304311 BRUSHCRKSS 230 304332 ASHEBOR230TT 230 1 | 1126 | 89.8 | 220.1 | 91.65 | 96.1 | Reconductor Asheboro-Ramseur Tap section of Asheboro-Siler City 115 kV line. Project 122 in 2023 CTPC Report
ctpc34w-PJM-DUKCPLE_rob2dn | 304696 SHAW AFB TAP 115 370238 3EASTOVER! 115 1 | 340/343 | 135 | 141 | SUMTER-SCE&G-WATEREE-PLANT-230KV-LINE | 192 | 76.1 | 135.3 | 96.98 | 95.93 | Reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F. Project 120 in 2023 CTPC Report
ctpc34w-TVA-DUK_rob2dn | 304696 SHAW AFB TAP 115 370238 3EASTOVER! 115 1 | 340/343 | 135 | 141 | SUMTER-SCE&G-WATEREE-PLANT-230KV-LINE | 200 | 76 | 135 | 96.83 | 95.76 | Reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F. Project 120 in 2023 CTPC Report

## Local Economic_DEC
Monitored Facility
Season | Transfer Case | Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | Base Rating (MVA) | Contingency Rating (MVA) | Base Flow (MVA) | Contingency Flow (MVA) | Final AC % Loading | Major Component Limited | Proposed Solution
3435w | MISO-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 62.1 | 208.1 | 121.6 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDYASH5VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 62.1 | 208.1 | 121.6 | Yes | Smart Relay Scheme
3435w | DUKCPLE-PJM | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 59.2 | 196.2 | 112.7 | Yes | Smart Relay Scheme
3435w | DUK-CPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 59.2 | 196.1 | 112.6 | Yes | Smart Relay Scheme
3435w | DUK-SOCO | STUDYVCS1VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 59.2 | 196.2 | 112.6 | Yes | Smart Relay Scheme
3435w | DUK-TVA | STUDYASH4VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 59.2 | 196.2 | 112.6 | Yes | Smart Relay Scheme
3435w | MISO-DUK | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 157 | 181 | 47.3 | 173 | 98 | Yes | Smart Relay Scheme
3435w | PJM-DUKCPLE | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 157 | 181 | 47.3 | 173 | 98 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDYASH5VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 157 | 181 | 47.3 | 173 | 98 | Yes | Smart Relay Scheme
3435w | TVA-DUK | STUDYASH7VRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 157 | 181 | 47.3 | 173 | 98 | Yes | Smart Relay Scheme
3435w | MISO-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 39.2 | 179.1 | 108.5 | Yes | Smart Relay Scheme
3435w | PJM-DUKCPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 39.2 | 179.1 | 108.5 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDYASH5VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 39.2 | 179 | 108.5 | Yes | Smart Relay Scheme
3435w | TVA-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 39.2 | 179.1 | 108.5 | Yes | Smart Relay Scheme
3435w | DUKCPLE-PJM | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 37.4 | 169.5 | 100.4 | Yes | Smart Relay Scheme
3435w | DUK-CPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 37.4 | 169.5 | 100.2 | Yes | Smart Relay Scheme
3435w | DUK-SOCO | STUDYVCS1VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 37.5 | 169.6 | 100.2 | Yes | Smart Relay Scheme
3435w | DUK-TVA | STUDYASH4VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 37.5 | 169.5 | 100.2 | Yes | Smart Relay Scheme
3435w | PJM-DUKCPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 59.3 | 199.6 | 120.2 | Yes | Smart Relay Scheme
3435w | TVA-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 59.3 | 199.6 | 120.2 | Yes | Smart Relay Scheme
3435w | MISO-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 59.3 | 199.6 | 120.1 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDYASH5VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 59.3 | 199.6 | 120.1 | Yes | Smart Relay Scheme
3435w | DUKCPLE-PJM | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 56.6 | 189 | 111.3 | Yes | Smart Relay Scheme
3435w | DUK-CPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 56.5 | 188.9 | 111.2 | Yes | Smart Relay Scheme
3435w | DUK-SOCO | STUDYVCS1VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 56.6 | 189.1 | 111.1 | Yes | Smart Relay Scheme
3435w | DUK-TVA | STUDYHAR1VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 157 | 181 | 56.6 | 189 | 111.1 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 92.8 | 135 | 106.2 | Yes | Already in CTPC Plan / Harley
3435w | TVA-DUK | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 91.5 | 133.2 | 104.7 | Yes | Already in CTPC Plan / Harley
3435w | DUK-TVA | THALGM | SHULERB | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 243.6 | 431.2 | 110.1 | No | Relay setting can be adjusted
3435w | DUK-TVA | THALGM | SHULERW | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 1 | 386 | 386 | 243.6 | 431.2 | 110.1 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | THALGM | SHULERB | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 238.2 | 421.7 | 107.7 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | THALGM | SHULERW | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 1 | 386 | 386 | 238.2 | 421.7 | 107.7 | No | Relay setting can be adjusted
3435w | DUK-SOCO | THALGM | SHULERB | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 227.4 | 402.5 | 102.8 | No | Relay setting can be adjusted
3435w | DUK-SOCO | THALGM | SHULERW | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 1 | 386 | 386 | 227.4 | 402.5 | 102.8 | No | Relay setting can be adjusted
3435w | DUK-CPLE | THALGM | SHULERB | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 216 | 382.2 | 97.5 | No | Relay setting can be adjusted
3435w | DUK-CPLE | THALGM | SHULERW | 306106 | 6JOCASSE 230.00 | 308489 | 6TUCKASE 230.00 | 1 | 386 | 386 | 216 | 382.2 | 97.5 | No | Relay setting can be adjusted
3435w | SOCO-DUK | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 18.7 | 129.7 | 106.9 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 17.5 | 129.7 | 106.8 | No | AEU (bus conductor)
3435w | PJM-DUKCPLE | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 16.9 | 129.7 | 106.7 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 16.1 | 129.7 | 106.6 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 30.3 | 122.9 | 98.9 | No | AEU (bus conductor)
3435w | DUK-TVA | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 29.2 | 122.9 | 98.9 | No | AEU (bus conductor)
3435w | DUK-SOCO | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 27.8 | 122.9 | 98.8 | No | AEU (bus conductor)
3435w | DUK-CPLE | STUDY | HORSHORUGB_B | 306120 | ASHVL HW 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 143 | 150 | 25.7 | 122.8 | 98.5 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 52.5 | 90.3 | 113.4 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-TVA | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 51.5 | 89.1 | 111.9 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-SOCO | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 50.3 | 87.5 | 109.7 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-CPLE | STUDY | CAMPHARLYBL | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 48.3 | 85.1 | 106.6 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | SOCO-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 43.2 | 77.6 | 104.5 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | TVA-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 42 | 77.1 | 103.7 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | PJM-DUKCPLE | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 41.3 | 76.9 | 103.3 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 306163 | HNDRSNVL 100.00 | 1 | 83 | 87 | 40.4 | 76.4 | 102.6 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | MISO-DUK | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 90.9 | 132.3 | 103.9 | Yes | Already in CTPC Plan / Harley
3435w | PJM-DUKCPLE | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 90.3 | 131.6 | 103.4 | Yes | Already in CTPC Plan / Harley
3435w | DUKCPLE-PJM | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 90.7 | 131.9 | 103.2 | Yes | Already in CTPC Plan / Harley
3435w | DUK-TVA | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 89.1 | 129.7 | 101.5 | Yes | Already in CTPC Plan / Harley
3435w | DUK-CPLE | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 88.7 | 129.1 | 100.8 | Yes | Already in CTPC Plan / Harley
3435w | DUK-SOCO | STUDYASH5VRS | HARLEYB-TIG_P21 | 306132 | CAMPOBEL 100.00 | 306198 | TIGER 100.00 | 1 | 83 | 132 | 87.8 | 127.8 | 99.9 | Yes | Already in CTPC Plan / Harley
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 157 | 166 | 90.3 | 169.1 | 107.4 | Yes | Rebuild Rugby B/W 100 kV lines between Horseshoe and Blantyre Retail (4.6 miles)
3435w | PJM-DUKCPLE | STUDY | HORSHORUGB_B | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 157 | 166 | 89.8 | 168 | 106.7 | Yes | Rebuild Rugby B/W 100 kV lines between Horseshoe and Blantyre Retail (4.6 miles)
3435w | DUKCPLE-PJM | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 56.1 | 87.1 | 106.7 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | SOCO-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 46.5 | 86.2 | 106.7 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-TVA | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 55.1 | 86.7 | 106.2 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | TVA-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 45.2 | 85.6 | 105.9 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | PJM-DUKCPLE | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 44.5 | 85.3 | 105.5 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-SOCO | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 53.8 | 86 | 105.3 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 43.5 | 84.8 | 104.9 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-CPLE | STUDY | HORSHORUGB_B | 306132 | CAMPOBEL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 51.7 | 84.8 | 103.7 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | SOCO-DUK | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 45.5 | 103.4 | 114.3 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 45.5 | 103.4 | 114.2 | No | AEU (bus conductor)
3435w | PJM-DUKCPLE | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 45.5 | 103.4 | 114.2 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 45.5 | 103.4 | 114.2 | No | AEU (bus conductor)
3435w | DUK-SOCO | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 44 | 99.6 | 108.7 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 44 | 99.5 | 108.6 | No | AEU (bus conductor)
3435w | DUK-TVA | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 44 | 99.6 | 108.6 | No | AEU (bus conductor)
3435w | DUK-CPLE | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 103 | 44 | 99.3 | 108.3 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 52 | 78.5 | 103.8 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | SOCO-DUK | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 42.6 | 77.1 | 103.8 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-TVA | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 51 | 78.2 | 103.3 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | TVA-DUK | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 41.4 | 76.6 | 103 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | PJM-DUKCPLE | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 40.7 | 76.4 | 102.6 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-SOCO | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 49.7 | 77.6 | 102.4 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 39.8 | 75.9 | 101.9 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | DUK-CPLE | STUDY | HORSHORUGB_B | 306163 | HNDRSNVL 100.00 | 307053 | BREC32 100.00 | 2 | 83 | 87 | 47.7 | 76.5 | 100.8 | No | Rebuild Hogback B/W 100 kV lines between Campobello and Hendersonville (17.9 miles)
3435w | MISO-DUK | STUDY | HORSHORUGB_B | 306164 | HORSESHO 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 143 | 150 | 56.3 | 129.9 | 95.6 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDY | HORSHORUGB_B | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 157 | 166 | 90.2 | 167.3 | 106.4 | Yes | Rebuild Rugby B/W 100 kV lines between Horseshoe and Blantyre Retail (4.6 miles)
3435w | SOCO-DUK | STUDY | HORSHORUGB_B | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 157 | 166 | 90.3 | 166 | 105.6 | Yes | Already in CTPC Plan / Harley
3435w | SOCO-DUK | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 93.9 | 142.3 | 109.1 | Yes | Already in CTPC Plan / Harley
3435w | TVA-DUK | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 92.6 | 140.6 | 107.6 | Yes | Already in CTPC Plan / Harley
3435w | MISO-DUK | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 92.1 | 139.8 | 107 | Yes | Already in CTPC Plan / Harley
3435w | PJM-DUKCPLE | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 91.5 | 139 | 106.4 | Yes | Already in CTPC Plan / Harley
3435w | DUKCPLE-PJM | STUDYASH5VRS | HARLEYW_P21 | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 97.7 | 137.6 | 105.7 | Yes | Already in CTPC Plan / Harley
3435w | DUK-TVA | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 89.8 | 136.1 | 103.9 | Yes | Already in CTPC Plan / Harley
3435w | DUK-CPLE | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 89.4 | 135.6 | 103.3 | Yes | Already in CTPC Plan / Harley
3435w | DUK-SOCO | STUDY | TGRTAYLORS_W | 306198 | TIGER 100.00 | 308709 | NEWCUTRET 100.00 | 2 | 126 | 132 | 88.5 | 134.3 | 102.4 | Yes | Already in CTPC Plan / Harley
3435w | DUK-SOCO | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 415.3 | 611.6 | 116.4 | Yes | Operating Solution
3435w | DUK-TVA | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 412.9 | 608 | 115.7 | Yes | Operating Solution
3435w | DUKCPLE-PJM | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 406 | 597.9 | 113.8 | Yes | Operating Solution
3435w | PJM-DUKCPLE | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 393 | 578.8 | 110.3 | Yes | Operating Solution
3435w | DUK-CPLE | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 391.7 | 576.5 | 109.8 | Yes | Operating Solution
3435w | TVA-DUK | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 388.4 | 571.8 | 109 | Yes | Operating Solution
3435w | SOCO-DUK | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 386.1 | 568.4 | 108.3 | Yes | Operating Solution
3435w | MISO-DUK | OCO3GM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 503 | 531 | 345.9 | 509.3 | 96.8 | Yes | Operating Solution
3435w | DUK-SOCO | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 415.3 | 611.6 | 116.4 | Yes | Operating Solution
3435w | DUK-TVA | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 412.9 | 608 | 115.7 | Yes | Operating Solution
3435w | DUKCPLE-PJM | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 406 | 597.9 | 113.8 | Yes | Operating Solution
3435w | PJM-DUKCPLE | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 393 | 578.8 | 110.3 | Yes | Operating Solution
3435w | DUK-CPLE | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 391.7 | 576.5 | 109.8 | Yes | Operating Solution
3435w | TVA-DUK | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 388.4 | 571.8 | 109 | Yes | Operating Solution
3435w | SOCO-DUK | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 386.1 | 568.4 | 108.3 | Yes | Operating Solution
3435w | MISO-DUK | OCO3GM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 503 | 531 | 345.9 | 509.3 | 96.8 | Yes | Operating Solution
3435w | MISO-DUK | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 85.3 | 172.4 | 100.9 | Yes | Operating Solution
3435w | SOCO-DUK | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 83.8 | 169.7 | 99.3 | Yes | Operating Solution
3435w | TVA-DUK | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 83.4 | 168.9 | 98.9 | Yes | Operating Solution
3435w | PJM-DUKCPLE | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 82.6 | 167.4 | 98 | Yes | Operating Solution
3435w | DUK-CPLE | STUDY | CLFSD5DNCN_B_FS | 306245 | CLIFSID 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 80.7 | 162.7 | 95.1 | Yes | Operating Solution
3435w | MISO-DUK | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 85 | 170.9 | 100.9 | Yes | Operating Solution
3435w | SOCO-DUK | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 83.4 | 168.2 | 99.3 | Yes | Operating Solution
3435w | TVA-DUK | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 83.1 | 167.5 | 98.8 | Yes | Operating Solution
3435w | PJM-DUKCPLE | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 82.3 | 166.1 | 98 | Yes | Operating Solution
3435w | DUK-CPLE | STUDY | CLFSD5DNCN_B_FS | 306253 | FAIRVIEW 100.00 | 306291 | PINKTPFV 100.00 | 1 | 157 | 166 | 80.5 | 161.2 | 95 | Yes | Operating Solution
3435w | DUK-SOCO | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 415.3 | 611.6 | 116.4 | Yes | Operating Solution
3435w | DUK-TVA | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 412.9 | 608 | 115.7 | Yes | Operating Solution
3435w | DUKCPLE-PJM | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 406 | 597.9 | 113.8 | Yes | Operating Solution
3435w | PJM-DUKCPLE | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 393 | 578.8 | 110.3 | Yes | Operating Solution
3435w | DUK-CPLE | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 391.7 | 576.5 | 109.8 | Yes | Operating Solution
3435w | TVA-DUK | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 388.4 | 571.8 | 109 | Yes | Operating Solution
3435w | SOCO-DUK | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 386.1 | 568.4 | 108.3 | Yes | Operating Solution
3435w | MISO-DUK | OCO3GM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 503 | 531 | 345.9 | 509.3 | 96.8 | Yes | Operating Solution
3435w | DUK-SOCO | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 415.3 | 611.6 | 116.4 | Yes | Operating Solution
3435w | DUK-TVA | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 412.9 | 608 | 115.7 | Yes | Operating Solution
3435w | DUKCPLE-PJM | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 406 | 597.9 | 113.8 | Yes | Operating Solution
3435w | PJM-DUKCPLE | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 393 | 578.8 | 110.3 | Yes | Operating Solution
3435w | DUK-CPLE | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 391.7 | 576.5 | 109.8 | Yes | Operating Solution
3435w | TVA-DUK | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 388.4 | 571.8 | 109 | Yes | Operating Solution
3435w | SOCO-DUK | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 386.1 | 568.4 | 108.3 | Yes | Operating Solution
3435w | MISO-DUK | OCO3GM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 503 | 531 | 345.9 | 509.3 | 96.8 | Yes | Operating Solution
3435w | MISO-DUK | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 188.3 | 130.2 | Yes | Radial - continue to monitor
3435w | PJM-DUKCPLE | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 188.3 | 130.2 | Yes | Radial - continue to monitor
3435w | PJM-DUKCPLE | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 60.8 | 124.8 | 113.8 | No | AEU (bus conductor)
3435w | SOCO-DUK | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 60.8 | 124.8 | 113.8 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 60.8 | 124.8 | 113.8 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 60.8 | 124.8 | 113.7 | No | AEU (bus conductor)
3435w | DUK-SOCO | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 58.5 | 119.5 | 108.2 | No | AEU (bus conductor)
3435w | DUK-CPLE | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 58.5 | 119.3 | 108.1 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 58.5 | 119.4 | 108.1 | No | AEU (bus conductor)
3435w | DUK-TVA | STUDY | PACOLET_LT2R | 306266 | LAUEC26 100.00 | 306286 | PACOLET 100.00 | 1 | 111 | 117 | 58.5 | 119.5 | 108.1 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 56.7 | 121.6 | 112 | No | AEU (bus conductor)
3435w | SOCO-DUK | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 56.7 | 121.5 | 112 | No | AEU (bus conductor)
3435w | PJM-DUKCPLE | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 56.7 | 121.5 | 111.9 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 56.7 | 121.5 | 111.9 | No | AEU (bus conductor)
3435w | DUK-SOCO | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 54.6 | 116.6 | 106.3 | No | AEU (bus conductor)
3435w | DUKCPLE-PJM | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 54.6 | 116.5 | 106.2 | No | AEU (bus conductor)
3435w | DUK-TVA | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 54.6 | 116.6 | 106.2 | No | AEU (bus conductor)
3435w | DUK-CPLE | STUDYASH7VRS | GLENSPW-PAC_P21 | 306286 | PACOLET 100.00 | 308478 | LAUEC36 100.00 | 1 | 111 | 117 | 54.6 | 116.5 | 106.1 | No | AEU (bus conductor)
3435w | MISO-DUK | BRECGM | CLI5 | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 119.3 | 96.2 | No | Radial - continue to monitor
3435w | SOCO-DUK | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 119.3 | 96.2 | No | Radial - continue to monitor
3435w | TVA-DUK | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 119.2 | 96.2 | No | Radial - continue to monitor
3435w | PJM-DUKCPLE | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 119.2 | 96.1 | No | Radial - continue to monitor
3435w | DUKCPLE-PJM | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 118.9 | 95.9 | No | Radial - continue to monitor
3435w | DUK-SOCO | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 118.9 | 95.9 | No | Radial - continue to monitor
3435w | DUK-TVA | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 118.9 | 95.9 | No | Radial - continue to monitor
3435w | DUK-CPLE | CLI5GM | BREC | 306287 | PEACH VY 100.00 | 308703 | DUK 308703 100.00 | 1 | 124 | 124 | - | 118.9 | 95.8 | No | Radial - continue to monitor
3435w | MISO-DUK | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 49.9 | 111.3 | 120.9 | No | Relay setting can be adjusted
3435w | SOCO-DUK | STUDYVCS1VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 49.9 | 111.3 | 120.8 | No | Relay setting can be adjusted
3435w | PJM-DUKCPLE | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 49.9 | 111.1 | 120.7 | No | Relay setting can be adjusted
3435w | TVA-DUK | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 50 | 111.1 | 120.7 | No | Relay setting can be adjusted
3435w | DUK-SOCO | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 48.2 | 107.1 | 114.8 | No | Relay setting can be adjusted
3435w | DUK-TVA | STUDY | PACOLET_LT2Y | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 48.2 | 107.1 | 114.6 | No | Relay setting can be adjusted
3435w | DUK-CPLE | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 48.2 | 106.9 | 114.5 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | STUDYASH7VRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 103 | 48.2 | 106.9 | 114.5 | No | Relay setting can be adjusted
3435w | TVA-DUK | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 188.3 | 130.2 | Yes | Radial - continue to monitor
3435w | SOCO-DUK | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 188.1 | 130 | Yes | Radial - continue to monitor
3435w | DUK-CPLE | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 180.9 | 123.6 | Yes | Radial - continue to monitor
3435w | DUK-SOCO | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 181.1 | 123.6 | Yes | Radial - continue to monitor
3435w | DUKCPLE-PJM | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 180.9 | 123.5 | Yes | Radial - continue to monitor
3435w | DUK-TVA | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 154 | 59.3 | 180.9 | 123.5 | Yes | Radial - continue to monitor
3435w | DUK-SOCO | STUDY | CLIFFSDE2P23MB | 306390 | DUK 306390 100.00 | 308793 | CLIFS2 100.00 | 1 | 126 | 132 | 37.3 | 129.4 | 96.5 | Yes | Rebuild Dairyhill B/W 100 kV lines between Cliffside and PPG Tap (7.7 miles)
3435w | DUK-TVA | STUDY | CLIFFSDE2P23MB | 306390 | DUK 306390 100.00 | 308793 | CLIFS2 100.00 | 1 | 126 | 132 | 37 | 129.1 | 96.3 | Yes | Rebuild Dairyhill B/W 100 kV lines between Cliffside and PPG Tap (7.7 miles)
3435w | DUKCPLE-PJM | STUDY | CLIFFSDE2P23MB | 306390 | DUK 306390 100.00 | 308793 | CLIFS2 100.00 | 1 | 126 | 132 | 36 | 128.1 | 95.6 | Yes | Rebuild Dairyhill B/W 100 kV lines between Cliffside and PPG Tap (7.7 miles)
3435w | DUKCPLE-PJM | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 1063 | 1063 | 598.7 | 1099.4 | 102.4 | Yes | Operating Solution
3435w | DUK-CPLE | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 1063 | 1063 | 591.9 | 1090.5 | 101.5 | Yes | Operating Solution
3435w | DUK-TVA | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 1063 | 1063 | 591.1 | 1089.2 | 101.4 | Yes | Operating Solution
3435w | DUK-SOCO | STUDY | LINCOLN12P23MB | 306441 | 6LINCOLN 230.00 | 308587 | 6ORCHARD 230.00 | 2 | 1063 | 1063 | 589.4 | 1087 | 101.2 | Yes | Operating Solution
3435w | MISO-DUK | STUDY | ANTIOCH41P23MB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 1 | 553 | 639 | 320.8 | 642.1 | 101.2 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | PJM-DUKCPLE | STUDY | ANTIOCH41P23MB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 1 | 553 | 639 | 319.4 | 639.1 | 100.7 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | MISO-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 197 | 208 | 140.2 | 233.7 | 110.4 | No | Add to CTPC Plan / Beulah RAS
3435w | PJM-DUKCPLE | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 197 | 208 | 129 | 215.3 | 101.7 | No | Add to CTPC Plan / Beulah RAS
3435w | TVA-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 197 | 208 | 125.6 | 209.9 | 99.1 | No | Add to CTPC Plan / Beulah RAS
3435w | SOCO-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 197 | 208 | 124.6 | 208.3 | 98.3 | No | Add to CTPC Plan / Beulah RAS
3435w | MISO-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 206.3 | 300 | 118.2 | No | Add to CTPC Plan / Beulah RAS
3435w | PJM-DUKCPLE | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 195 | 281.6 | 111 | No | Add to CTPC Plan / Beulah RAS
3435w | TVA-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 191.7 | 276.2 | 108.8 | No | Add to CTPC Plan / Beulah RAS
3435w | SOCO-DUK | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 190.8 | 274.6 | 108.2 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-SOCO | STUDYASH4VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 177.2 | 254.5 | 99.9 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-TVA | STUDYASH4VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 176.2 | 252.7 | 99.2 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-CPLE | STUDYASH4VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 175.5 | 251.7 | 98.8 | No | Add to CTPC Plan / Beulah RAS
3435w | DUKCPLE-PJM | STUDYASH4VRS | BEULAHWH-STA_P21 | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 249 | 171.6 | 245.2 | 96.3 | No | Add to CTPC Plan / Beulah RAS
3435w | MISO-DUK | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 140.1 | 271 | 128.6 | No | Add to CTPC Plan / Beulah RAS
3435w | PJM-DUKCPLE | STUDY | STAMEYOXFORD | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 130.7 | 256.4 | 121.7 | No | Add to CTPC Plan / Beulah RAS
3435w | TVA-DUK | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 127.3 | 251.7 | 119.4 | No | Add to CTPC Plan / Beulah RAS
3435w | SOCO-DUK | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 126.3 | 250.3 | 118.8 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-SOCO | STUDYASH4VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 123.2 | 234.5 | 110.2 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-TVA | STUDYASH4VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 122.1 | 232.8 | 109.4 | No | Add to CTPC Plan / Beulah RAS
3435w | DUK-CPLE | STUDYASH4VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 121.5 | 231.7 | 108.9 | No | Add to CTPC Plan / Beulah RAS
3435w | DUKCPLE-PJM | STUDYASH4VRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 197 | 208 | 117.5 | 225.3 | 105.9 | No | Add to CTPC Plan / Beulah RAS
3435w | MISO-DUK | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 148.6 | 300 | 118.2 | No | Relay setting can be adjusted
3435w | PJM-DUKCPLE | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 137.3 | 281.6 | 111 | No | Relay setting can be adjusted
3435w | TVA-DUK | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 133.9 | 276.2 | 108.8 | No | Relay setting can be adjusted
3435w | SOCO-DUK | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 133 | 274.6 | 108.2 | No | Relay setting can be adjusted
3435w | DUK-SOCO | STUDYASH4VRS | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 123.1 | 254.4 | 99.9 | No | Relay setting can be adjusted
3435w | DUK-TVA | STUDYASH4VRS | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 122.1 | 252.7 | 99.2 | No | Relay setting can be adjusted
3435w | DUK-CPLE | STUDYASH4VRS | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 121.5 | 251.7 | 98.8 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | STUDYASH4VRS | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 249 | 117.5 | 245.2 | 96.2 | No | Relay setting can be adjusted
3435w | TVA-DUK | STUDY | ANTIOCH41P23MB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 1 | 553 | 639 | 312.9 | 622.5 | 97.9 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | SOCO-DUK | STUDY | ANTIOCH41P23MB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 1 | 553 | 639 | 311.4 | 618.6 | 97.3 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | MISO-DUK | OXFDGM | HORSEGAPB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 2 | 553 | 639 | 325.2 | 625.1 | 98.3 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | PJM-DUKCPLE | OXFDGM | HORSEGAPB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 2 | 553 | 639 | 323.8 | 622.6 | 97.9 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | TVA-DUK | OXFDGM | HORSEGAPB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 2 | 553 | 639 | 317.4 | 610.4 | 95.8 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | SOCO-DUK | OXFDGM | HORSEGAPB | 306712 | 6ANTIOCH 230.00 | 306715 | 6WILKESTIE 230.00 | 2 | 553 | 639 | 315.9 | 607.5 | 95.4 | Yes | Rebuild Horse Gap B/W 230 kV line between Antioch and Wilkes Tie (4.3 miles)
3435w | PJM-DUKCPLE | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.3 | 84 | 140.1 | Yes | Add to CTPC Plan / Tiger
3435w | TVA-DUK | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.3 | 83.8 | 139.7 | Yes | Add to CTPC Plan / Tiger
3435w | SOCO-DUK | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 149.4 | 327.3 | 97 | No | AEU (switch and bus conductor)
3435w | TVA-DUK | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 149.1 | 326.5 | 96.7 | No | AEU (switch and bus conductor)
3435w | PJM-DUKCPLE | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 147.7 | 323.1 | 95.7 | No | AEU (switch and bus conductor)
3435w | DUKCPLE-PJM | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 146.8 | 322.8 | 95.5 | No | AEU (switch and bus conductor)
3435w | MISO-DUK | STUDY | BECKRDT_LT1Y | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z1 | 292 | 319 | 147.4 | 322.3 | 95.5 | No | AEU (switch and bus conductor)
3435w | SOCO-DUK | STUDY | BECKRDT_LT1R | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z2 | 292 | 319 | 149.4 | 319 | 95.3 | No | AEU (switch and bus conductor)
3435w | TVA-DUK | STUDY | BECKRDT_LT1R | 306726 | BECKRDIT 100.00 | 309506 | BECK2 100.00 | Z2 | 292 | 319 | 149.1 | 318.1 | 95 | No | AEU (switch and bus conductor)
3435w | PJM-DUKCPLE | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 166 | 213 | 118.6 | 217.3 | 98.5 | No | Add to CTPC Plan / Bethania + Shattalon
3435w | MISO-DUK | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 166 | 213 | 118.5 | 216.7 | 98.2 | No | Add to CTPC Plan / Bethania + Shattalon
3435w | TVA-DUK | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 166 | 213 | 115.4 | 211.4 | 95.7 | No | Add to CTPC Plan / Bethania + Shattalon
3435w | SOCO-DUK | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 166 | 213 | 114.8 | 210.2 | 95.2 | No | Add to CTPC Plan / Bethania + Shattalon
3435w | PJM-DUKCPLE | STUDY | RURLHLL_LT3R | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 111 | 117 | 79.1 | 116 | 100.9 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDY | RURLHLL_LT3R | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 111 | 117 | 78.2 | 115.4 | 100.4 | No | AEU (bus conductor)
3435w | TVA-DUK | STUDY | RURLHLL_LT3R | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 111 | 117 | 77.2 | 114.8 | 99.8 | No | AEU (bus conductor)
3435w | SOCO-DUK | STUDY | RURLHLL_LT3R | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 111 | 117 | 76.9 | 114.6 | 99.6 | No | AEU (bus conductor)
3435w | MISO-DUK | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 52.6 | 171.1 | 108 | No | Revised rating is 219 MVA
3435w | PJM-DUKCPLE | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 51.6 | 171.2 | 108 | No | Revised rating is 219 MVA
3435w | SOCO-DUK | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 47.2 | 171 | 107.7 | No | Revised rating is 219 MVA
3435w | TVA-DUK | STUDYOXFDGC | OXFRDBRMTN_W_FS | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 48.1 | 170.9 | 107.7 | No | Revised rating is 219 MVA
3435w | DUKCPLE-PJM | STUDY | OXFRDBRMTN_W_NOGEN_F | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 26 | 160.4 | 100.4 | No | Revised rating is 219 MVA
3435w | DUK-SOCO | STUDY | OXFRDBRMTN_W_NOGEN_F | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 31 | 159.8 | 99.7 | No | Revised rating is 219 MVA
3435w | DUK-TVA | STUDY | OXFRDBRMTN_W_NOGEN_F | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 30.1 | 159.8 | 99.7 | No | Revised rating is 219 MVA
3435w | DUK-CPLE | STUDY | OXFRDBRMTN_W_NOGEN_F | 306813 | WILKES T 100.00 | 306817 | CAIRO T 100.00 | 1 | 166 | 166 | 31.6 | 159.6 | 99.6 | No | Revised rating is 219 MVA
3435w | PJM-DUKCPLE | STUDY | PLGARDN_LT1R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 17.9 | 152.3 | 102.6 | No | Required Customer upgrade addresses issue
3435w | SOCO-DUK | STUDY | PLGARDN_LT2R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 16.9 | 152.2 | 102.5 | No | Required Customer upgrade addresses issue
3435w | TVA-DUK | STUDY | PLGARDN_LT2R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 17.2 | 152.2 | 102.5 | No | Required Customer upgrade addresses issue
3435w | MISO-DUK | STUDY | PLGARDN_LT2R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 20.1 | 152.2 | 102.4 | No | Required Customer upgrade addresses issue
3435w | DUK-CPLE | STUDY | PLGARDN_LT2R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 11.1 | 148.6 | 99.6 | No | Required Customer upgrade addresses issue
3435w | DUKCPLE-PJM | STUDY | PLGARDN_LT1R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 10.6 | 148.6 | 99.5 | No | Required Customer upgrade addresses issue
3435w | DUK-SOCO | STUDY | PLGARDN_LT3R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 12 | 148.6 | 99.4 | No | Required Customer upgrade addresses issue
3435w | DUK-TVA | STUDY | PLGARDN_LT3R | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 146 | 159 | 11.8 | 148.6 | 99.4 | No | Required Customer upgrade addresses issue
3435w | DUK-CPLE | BEL1GM | PARKWOOD_EHV | 306848 | 6PL GRDN 230.00 | 306850 | 8PL GRDN 500.00 | 5 | 1519 | 1519 | 858.6 | 1443.3 | 95 | No | Relay setting can be adjusted
3435w | SOCO-DUK | BEL1GM | PARKWOOD_EHV | 306848 | 6PL GRDN 230.00 | 306850 | 8PL GRDN 500.00 | 5 | 1519 | 1519 | 904.1 | 1443.4 | 95 | No | Relay setting can be adjusted
3435w | MISO-DUK | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 151.9 | 275.2 | 133.3 | No | Required Customer upgrade addresses issue
3435w | PJM-DUKCPLE | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 149.5 | 272.1 | 132 | No | Required Customer upgrade addresses issue
3435w | TVA-DUK | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 148.9 | 271.4 | 131.5 | No | Required Customer upgrade addresses issue
3435w | SOCO-DUK | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 148.6 | 271 | 131.4 | No | Required Customer upgrade addresses issue
3435w | DUK-SOCO | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 138.8 | 256.4 | 124.1 | No | Required Customer upgrade addresses issue
3435w | DUK-TVA | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 138.5 | 256 | 123.9 | No | Required Customer upgrade addresses issue
3435w | DUKCPLE-PJM | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 136.6 | 253.7 | 123 | No | Required Customer upgrade addresses issue
3435w | DUK-CPLE | STUDY | PLGDNRDLMN_W | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 207 | 136.5 | 253.4 | 122.9 | No | Required Customer upgrade addresses issue
3435w | MISO-DUK | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 139.8 | 268.6 | 131.4 | No | Required Customer upgrade addresses issue
3435w | PJM-DUKCPLE | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 137.2 | 264.8 | 129.7 | No | Required Customer upgrade addresses issue
3435w | TVA-DUK | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 136.6 | 264.4 | 129.5 | No | Required Customer upgrade addresses issue
3435w | SOCO-DUK | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 136.2 | 264.1 | 129.3 | No | Required Customer upgrade addresses issue
3435w | DUK-SOCO | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 134.4 | 254.8 | 122.2 | No | Required Customer upgrade addresses issue
3435w | DUK-TVA | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 134.1 | 254.4 | 122.1 | No | Required Customer upgrade addresses issue
3435w | DUK-CPLE | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 132 | 252.1 | 121.2 | No | Required Customer upgrade addresses issue
3435w | DUKCPLE-PJM | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 207 | 132.1 | 252.3 | 121.1 | No | Required Customer upgrade addresses issue
3435w | MISO-DUK | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.3 | 83.7 | 139.6 | Yes | Add to CTPC Plan / Tiger
3435w | SOCO-DUK | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 25.3 | 83.7 | 139.4 | Yes | Add to CTPC Plan / Tiger
3435w | DUK-SOCO | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 24.3 | 82.4 | 137.4 | Yes | Add to CTPC Plan / Tiger
3435w | DUK-TVA | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 24.3 | 82.1 | 136.8 | Yes | Add to CTPC Plan / Tiger
3435w | DUKCPLE-PJM | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 24.3 | 81.8 | 136.3 | Yes | Add to CTPC Plan / Tiger
3435w | DUK-CPLE | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 50 | 60 | 24.2 | 81.7 | 136.2 | Yes | Add to CTPC Plan / Tiger
3435w | MISO-DUK | CLI5GM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 20.7 | 60.6 | 108.3 | Yes | Operating Solution
3435w | PJM-DUKCPLE | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 20.5 | 60.6 | 108.2 | Yes | Operating Solution
3435w | SOCO-DUK | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 20.5 | 60.6 | 108.2 | Yes | Operating Solution
3435w | TVA-DUK | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 20.5 | 60.6 | 108.2 | Yes | Operating Solution
3435w | DUKCPLE-PJM | CLI5GM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 19.4 | 57.8 | 103.2 | Yes | Operating Solution
3435w | DUK-SOCO | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 19.2 | 57.8 | 103.2 | Yes | Operating Solution
3435w | DUK-TVA | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 19.2 | 57.8 | 103.2 | Yes | Operating Solution
3435w | DUK-CPLE | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 19.2 | 57.7 | 103.1 | Yes | Operating Solution
3435w | MISO-DUK | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 50.1 | 91.6 | 109.1 | Yes | Operating Solution
3435w | PJM-DUKCPLE | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 50.1 | 91.6 | 109 | Yes | Operating Solution
3435w | TVA-DUK | STUDY | LAURENRAB_B_CS#_TGLC | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 41.6 | 21.7 | 40.2 | 98.1 | No | Relay setting can be adjusted
3435w | MISO-DUK | STUDY | LAURENCLN_W_CS#_TGLC | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 41.6 | 21.7 | 39.9 | 96.8 | No | Relay setting can be adjusted
3435w | PJM-DUKCPLE | STUDY | LAURENCLN_W_CS#_TGLC | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 41.6 | 21.8 | 39.9 | 96.8 | No | Relay setting can be adjusted
3435w | SOCO-DUK | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 50.1 | 91.6 | 109 | Yes | Operating Solution
3435w | TVA-DUK | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 50.1 | 91.6 | 109 | Yes | Operating Solution
3435w | DUK-SOCO | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 47.6 | 87 | 103.6 | Yes | Operating Solution
3435w | DUK-TVA | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 47.6 | 87 | 103.6 | Yes | Operating Solution
3435w | DUK-CPLE | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 47.6 | 87 | 103.5 | Yes | Operating Solution
3435w | DUKCPLE-PJM | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 84 | 47.6 | 87 | 103.5 | Yes | Operating Solution
3435w | MISO-DUK | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 47.9 | 90.9 | 119.7 | Yes | Operating Solution
3435w | PJM-DUKCPLE | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 47.9 | 90.9 | 119.6 | Yes | Operating Solution
3435w | SOCO-DUK | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 47.9 | 90.9 | 119.6 | Yes | Operating Solution
3435w | TVA-DUK | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 47.9 | 90.9 | 119.6 | Yes | Operating Solution
3435w | DUK-SOCO | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 45.5 | 86.4 | 113.7 | Yes | Operating Solution
3435w | DUK-TVA | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 45.5 | 86.4 | 113.7 | Yes | Operating Solution
3435w | DUK-CPLE | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 45.5 | 86.3 | 113.6 | Yes | Operating Solution
3435w | DUKCPLE-PJM | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 76 | 45.5 | 86.3 | 113.6 | Yes | Operating Solution
3435w | MISO-DUK | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 42.6 | 89.7 | 105.5 | Yes | Operating Solution
3435w | PJM-DUKCPLE | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 42.6 | 89.7 | 105.5 | Yes | Operating Solution
3435w | SOCO-DUK | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 42.6 | 89.6 | 105.5 | Yes | Operating Solution
3435w | TVA-DUK | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 42.6 | 89.6 | 105.5 | Yes | Operating Solution
3435w | DUK-SOCO | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 40.6 | 85.6 | 100.7 | Yes | Operating Solution
3435w | DUK-TVA | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 40.6 | 85.6 | 100.7 | Yes | Operating Solution
3435w | DUK-CPLE | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 40.6 | 85.5 | 100.6 | Yes | Operating Solution
3435w | DUKCPLE-PJM | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 85 | 40.6 | 85.5 | 100.6 | Yes | Operating Solution
3435w | PJM-DUKCPLE | STUDYHAR1VRS | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.8 | 47.8 | 119.6 | Yes | Operating Solution
3435w | SOCO-DUK | STUDYHAR1VRS | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.9 | 47.8 | 119.6 | Yes | Operating Solution
3435w | TVA-DUK | STUDYHAR1VRS | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.9 | 47.8 | 119.6 | Yes | Operating Solution
3435w | MISO-DUK | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.7 | 47.8 | 119.5 | Yes | Operating Solution
3435w | DUK-SOCO | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.2 | 45.5 | 113.7 | Yes | Operating Solution
3435w | DUK-TVA | STUDY | ENO230HT1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.2 | 45.5 | 113.7 | Yes | Operating Solution
3435w | DUK-CPLE | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.3 | 45.4 | 113.6 | Yes | Operating Solution
3435w | DUKCPLE-PJM | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 40 | 16.3 | 45.4 | 113.6 | Yes | Operating Solution
3435w | DUKCPLE-PJM | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 308940 | R TRNGLE_W 100.00 | 1 | 154 | 162 | 85.4 | 154.6 | 96 | Yes | Add to CTPC Plan / Delta
3435w | DUK-CPLE | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 308940 | R TRNGLE_W 100.00 | 1 | 154 | 162 | 85.5 | 153.7 | 95 | Yes | Add to CTPC Plan / Delta
3435w | DUK-TVA | NANTGM | NANT_L03 | 308487 | 5TUCKASE 161.00 | 308488 | 5WEBSTER 161.00 | 1 | 386 | 386 | 272.7 | 399.4 | 102.9 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | NANTGM | NANT_L03 | 308487 | 5TUCKASE 161.00 | 308488 | 5WEBSTER 161.00 | 1 | 386 | 386 | 266.7 | 390.2 | 100.5 | No | Relay setting can be adjusted
3435w | DUK-SOCO | NANTGM | NANT_L03 | 308487 | 5TUCKASE 161.00 | 308488 | 5WEBSTER 161.00 | 1 | 386 | 386 | 254.6 | 371.6 | 95.5 | No | Relay setting can be adjusted
3435w | DUK-TVA | THALGM | TUCKASEEBK3 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 244.4 | 447.5 | 115.9 | No | Relay setting can be adjusted
3435w | DUK-TVA | THALGM | TUCKASEEBK2 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 3 | 386 | 386 | 242.9 | 447.1 | 115.8 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | THALGM | TUCKASEEBK3 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 239.1 | 437.9 | 113.4 | No | Relay setting can be adjusted
3435w | DUKCPLE-PJM | THALGM | TUCKASEEBK2 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 3 | 386 | 386 | 237.7 | 437.5 | 113.3 | No | Relay setting can be adjusted
3435w | DUK-SOCO | THALGM | TUCKASEEBK3 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 228.4 | 418.4 | 108.4 | No | Relay setting can be adjusted
3435w | DUK-SOCO | THALGM | TUCKASEEBK2 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 3 | 386 | 386 | 227.1 | 418 | 108.3 | No | Relay setting can be adjusted
3435w | DUK-CPLE | THALGM | TUCKASEEBK3 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 2 | 386 | 386 | 217.1 | 397.6 | 103 | No | Relay setting can be adjusted
3435w | DUK-CPLE | THALGM | TUCKASEEBK2 | 308487 | 5TUCKASE 161.00 | 308489 | 6TUCKASE 230.00 | 3 | 386 | 386 | 215.8 | 397.2 | 102.9 | No | Relay setting can be adjusted
3435w | PJM-DUKCPLE | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 62.1 | 208.1 | 121.7 | Yes | Smart Relay Scheme
3435w | TVA-DUK | STUDYASH7VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 157 | 181 | 62.1 | 208.1 | 121.7 | Yes | Smart Relay Scheme
3435w | SOCO-DUK | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 266.3 | 445.9 | 107.4 | No | AEU (CT)
3435w | TVA-DUK | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 265.7 | 445.1 | 107.3 | No | AEU (CT)
3435w | MISO-DUK | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 265.3 | 444.4 | 107.1 | No | AEU (CT)
3435w | PJM-DUKCPLE | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 265 | 444 | 107 | No | AEU (CT)
3435w | DUK-CPLE | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 248.3 | 416.4 | 100.3 | No | AEU (CT)
3435w | DUKCPLE-PJM | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 247.1 | 414.2 | 99.8 | No | AEU (CT)
3435w | DUK-TVA | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 246.7 | 413.7 | 99.7 | No | AEU (CT)
3435w | DUK-SOCO | STUDY | CENTFISHWH | 309405 | 1CENTRL 1 1.0000 | 309501 | CENT1 100.00 | 1 | 415 | 415 | 246.2 | 413.1 | 99.6 | No | AEU (CT)
3435w | SOCO-DUK | STUDYASH5VRS | PISGAH2 | 309450 | 1PISGA 1 1.0000 | 309513 | PISG1 100.00 | 1 | 220 | 246 | 154.1 | 234.3 | 95.3 | No | AEU (CT)
3435w | SOCO-DUK | STUDYASH5VRS | PISGAH1 | 309451 | 1PISGA 2 1.0000 | 309514 | PISG2 100.00 | 2 | 246 | 246 | 157 | 236.4 | 96.1 | No | AEU (CT)
3435w | TVA-DUK | LECCGM | PISGAH1 | 309451 | 1PISGA 2 1.0000 | 309514 | PISG2 100.00 | 2 | 246 | 246 | 156.2 | 234.1 | 95.2 | No | AEU (CT)
3435w | DUKCPLE-PJM | LECCGM | PISGAH1 | 309451 | 1PISGA 2 1.0000 | 309514 | PISG2 100.00 | 2 | 246 | 246 | 155.8 | 233.6 | 95 | No | AEU (CT)
3435w | MISO-DUK | LECCGM | PISGAH1 | 309451 | 1PISGA 2 1.0000 | 309514 | PISG2 100.00 | 2 | 246 | 246 | 155.9 | 233.7 | 95 | No | AEU (CT)

## Projects to Add to Plan
Project | Region | ISD | Estimated Cost
Fayetteville 230/115kV bank #1, increase CT ratios and relay settings to allow 336 MVA rating | DEP | 2024-12-01 | 3000000
Sutton – Wilmington Ninth & Orange section of the Sutton – Castle Hayne 230kV line, Upgrade line switch | DEP | 2024-12-13 | 1000000
Richmond 500, upgrade 230kV wave trap, disconnect switches, and CT ratio to 3000A for the Laurinburg-Richmond 230kV line | DEP | 2025-03-10 | 1100000
Sutton-Wallace 230kV line, Raise Crooked Run Solar-Wallace section to 212F and increase CT ratios and relay settings at Wallace 230 | DEP | 2025-04-11 | 800000
Richmond 500, Change the CT ratios on Richmond 500/230kV banks 1 & 2 | DEP | 2025-05-08 | 3700000
Jacksonville - Jacksonville City 115kV East Line, Uprate CT Ratio at Jacksonville | DEP | 2025-10-17 | 200000
Henderson 230/115kV banks #1 & #2, increase CT ratios and relay settings to allow 336 MVA rating | DEP | 2025-11-20 | 2900000
Havelock 230, upgrade 115kV disconnect switches, wave traps, and CT ratios | DEP | 2025-12-01 | 7200000
Vanderbilt- West Asheville 115kV, Upgrade 115kV CB and Switches to 2000 A | DEP | 2025-12-08 | 2000000
Clayton Industrial - Selma 115kV Line, Reconductor entire line (RZEP 2.0) | DEP | 2027-11-18 | 24900000
Brunswick 1 - Delco 230kV East line, Upgrade switch #1-1 to 2000 A, Reconductor 0.09-mi Brunswick 1 - Southport Tap section with 6-1590 MCM ACSR | DEP | 2028-05-08 | 3600000
Goldsboro 115kV Switching Station, Increase CT Ratio and Relay Settings on the Goldsboro-Wommack 115kV line | DEP | 2028-06-07 | 200000
Lilesville - Oakboro 230kV Black & White lines, Reconductor entire lines (RZEP 2.0) | DEP | 2028-06-23 | 104700000
Brunswick 2 - Delco 230kV West line, Raise 2.3-mile Brunswick 2 - BEMC Southport section to 212F | DEP | 2029-06-27 | 1900000
Lee - Milburnie 230: Rebuild 23.78 miles from Lee - Powhatan Industrial Tap with 6-1590 ACSR and upgrade terminal equipment at Lee 230 to 3000A (DISIS 2023 or RZEP 2.0) | DEP | 2031-12-11 | 57500000
Woodlawn 230/100/44 kV Tie Station, Upgrade | DEC | 2024-06-01 | 1700000
Bethania and Shattalon 100 kV Lines, RAS | DEC | 2025-02-06 | 600000
Davidson River 100 kV Lines, RAS | DEC | 2025-04-07 | 800000
Batte 100 kV Line, RAS | DEC | 2025-05-29 | 1200000
Kennedy 100 kV Line, RAS | DEC | 2025-07-08 | 400000
Timber 100 kV Line and Sherrill 100 kV Line, RAS | DEC | 2025-11-01 | 400000
Nanny Mountain 1 44 kV Line, Upgrade and Partial Conversion to 100 kV | DEC | 2026-05-26 | 5500000
Pinewood 100 kV Line, RAS | DEC | 2026-06-01 | 500000
Cherokee 100 kV Line (Peach Valley-Enola Retail), Upgrade | DEC | 2026-06-01 | 5100000
Earl 100 kV Line (Customer Tap-Customer Tap), Upgrade | DEC | 2026-06-25 | 6400000
Crest St 100 kV Lines, Raise | DEC | 2027-04-28 | 1900000
Swepsonville 100 kV Line (Mebane-Trollingwood Retail), Upgrade | DEC | 2028-04-06 | 3000000
Lakewood 100 kV Line (Lakewood-Remount Road Retail), Upgrade | DEC | 2028-04-07 | 1700000
Gastonia # 2 44 kV Line, Upgrade | DEC | 2028-05-10 | 20700000
Ashe St 100 kV Line (Durham-Ashe St), Upgrade | DEC | 2028-06-01 | 8000000
Bush River Tie 115/100 kV, Upgrade [RZEP 2.0] | DEC | 2028-06-01 | 11400000
Broadway B/W 100 kV (Belton-Lee) [RZEP 2.0] | DEC | 2028-06-01 | 19800000
Champion B/W 100 kV (Bush River-Newberry PV), Upgrade [RZEP 2.0] | DEC | 2028-06-01 | 29100000
Tiger Tie AT5 Upgrade | DEC | 2028-07-07 | 6900000
Delta 100 kV Line, RAS | DEC | 2028-08-21 | 800000
Oak Hollow Switching Station, Construct | DEC | 2028-10-25 | 5100000
Batte 100 kV Line (Concord-Winecoff), Upgrade | DEC | 2029-03-22 | 1600000
Delta 100 kV Line (Research Triangle Retail-Ellis Rd Retail), Upgrade | DEC | 2029-05-11 | 2500000
Harrisburg 230/100/44 kV Tie Station, Upgrade | DEC | 2029-05-25 | 9100000
Beulah 100 kV Line, RAS | DEC | 2029-06-01 | 500000
Sycamore B/W 100 kV (Longview-Lyle Creek), Upgrade and Network | DEC | 2029-06-01 | 7700000
Hodges 230/100/44 kV Tie, Upgrade | DEC | 2029-08-24 | 6100000
Lilesville B/W 230 kV (Oakboro-*DEP), Upgrade [RZEP 2.0] | DEC | 2029-12-01 | 30200000
Pinewood 100 kV Line (Lawsons Fork-Una Retail), Upgrade | DEC | 2030-05-06 | 2100000
E Durham 230/100 kV Tie, Establish Panther Line Terminals [Modification to 0096 in 2023 Plan - splitting into two projects] | DEC | 2030-06-01 | 800000
States CTCC Bus Line 4, Add | DEC | 2030-08-06 | 3100000
Dairyhill 100 kV Line (Shelby-PPG Tap), Upgrade | DEC | 2030-10-16 | 9000000
Troutman 44 kV Line, Upgrade and Partial conversion to 100 kV [Modification to 0110 in 2023 Plan - additional scope] | DEC | 2031-05-26 | 64800000
Marshall 230 kV Line (Marshall-Beckerdite), Raise | DEC | 2033-07-08 | 200000
Ferrell Wh 100 kV Line, Add | DEC | TBD | 600000
Steam 100 kV Line (Dan River CC-Dan River Steam), Upgrade | DEC | TBD | 1000000
Madison Tie, Upgrade | DEC | TBD | 2400000
Shelby 230/100/44 kV Tie, Upgrade | DEC | TBD | 6400000
Central 230/100/44 kV Tie, Upgrade | DEC | TBD | 10000000
Bethania and Shattalon 100 kV Lines (Rural Hall-Shattalon), Upgrade | DEC | TBD | 12800000
Panther 100 kV Lines (Parkwood Tie - E Durham Tie), Upgrade and Network to E Durham Tie [Modification to 0096 in 2023 Plan - splitting into two projects] | DEC | TBD | 55700000
DEP Total Estimated Cost |  |  | 214700000
DEC Total Estimated Cost |  |  | 357600000
DEP + DEC Total Estimated Cost |  |  | 572300000