## Notes
MVST Cases |  |  |  |  | MVST Resource Dispatch
Scenario | Case | Description | Type | Notes | MVST Resource | Summer Mid-Day | Summer Peak | Winter Peak
1 | ctpc34s_r3_MVST_Scenario1_SP | Summer Peak | Base | Solar at 80% DEC, 50% DEP | Solar | 100% | 80% / 50% | 0%
1 | ctpc34s_r3_MVST_Scenario1_S90 | Summer Peak scaled down 10% | Sensitivity |  | Storage paired with Solar | -100% | 0% | 100%
1 | ctpc34s_r3_MVST_Scenario1_S110 | Summer Peak scaled up 10% | Sensitivity |  | Standalone Battery | -100% | 0% | 100%
1 | ctpc34s_r3_MVST_Scenario1_CSM | Charging Summer Midday at 90% of Peak Load | Base | Solar at 100% | On-Shore Wind | 40% / 60% | 40% / 60% | 85% / 100%
1 | ctpc34w_r3_MVST_Scenario1_WP | Winter Peak | Base |  | Off-Shore Wind | 100% | 100% | 100%
1 | ctpc34w_r3_MVST_Scenario1_W90 | Winter Peak scaled down 10% | Sensitivity |  | Small Modular Reactor (SMR) | n/a | n/a | 100%
1 | ctpc34w_r3_MVST_Scenario1_W110 | Winter Peak scaled up 10% | Sensitivity |  | Pumped Storage (PSH) | -100% | 100% | 100%
1 | ctpc34s_r3_MVST_Scenario1_SP_OFW | Summer Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity |  | Combined Cycle (CC)* | 100% | 100% | 100%
1 | ctpc34w_r3_MVST_Scenario1_WP_OFW | Winter Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity |  | Combustion Turbine (CT) | 0% | 0% | 100%
2 | ctpc34s_r3_MVST_Scenario2_SP | Summer Peak | Base | Solar at 80% DEC, 50% DEP
2 | ctpc34s_r3_MVST_Scenario2_S90 | Summer Peak scaled down 10% | Sensitivity |  | *MVST CCs are backed down to solve the case for some 90% load sensitivity cases
2 | ctpc34s_r3_MVST_Scenario2_S110 | Summer Peak scaled up 10% | Sensitivity
2 | ctpc34s_r3_MVST_Scenario2_CSM | Charging Summer Midday at 90% of Peak Load | Base | Solar at 100%
2 | ctpc34w_r3_MVST_Scenario2_WP | Winter Peak | Base
2 | ctpc34w_r3_MVST_Scenario2_W90 | Winter Peak scaled down 10% | Sensitivity
2 | ctpc34w_r3_MVST_Scenario2_W110 | Winter Peak scaled up 10% | Sensitivity
2 | ctpc34s_r3_MVST_Scenario2_SP_OFW | Summer Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity
2 | ctpc34w_r3_MVST_Scenario2_WP_OFW | Winter Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity
3 | ctpc34s_r3_MVST_Scenario3_SP | Summer Peak | Base | Solar at 80% DEC, 50% DEP
3 | ctpc34s_r3_MVST_Scenario3_S90 | Summer Peak scaled down 10% | Sensitivity
3 | ctpc34s_r3_MVST_Scenario3_S110 | Summer Peak scaled up 10% | Sensitivity
3 | ctpc34s_r3_MVST_Scenario3_CSM | Charging Summer Midday at 90% of Peak Load | Base | Solar at 100%
3 | ctpc34w_r3_MVST_Scenario3_WP | Winter Peak | Base
3 | ctpc34w_r3_MVST_Scenario3_W90 | Winter Peak scaled down 10% | Sensitivity
3 | ctpc34w_r3_MVST_Scenario3_W110 | Winter Peak scaled up 10% | Sensitivity
3 | ctpc34s_r3_MVST_Scenario3_SP_OFW | Summer Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity
3 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Winter Peak Sensitivity with additional 2400 MW of Offshore Wind at Sutton North | Sensitivity
Major Resources Included
Company | Generation Facility | 2034S | 2034/35 W
DEC | Generic CC (at Marshall) | Included | Included
DEC | Anderson CC | Included | Included
DEC | Generic CC (at Buck) - Portfolio P3 Only | Included | Included | - Scenario 2 and 3
DEC | Belews Creek CTs | Included | Included
DEC | Buck CTs | Included | Included
DEC | Pumped Storage Hydro Bad Creek II | Included | Included
DEC | Belews Creek SMR | Not Included | Included
DEP | Person County CC #2 - Portfolio P3 Only | Included | Included | - Scenario 2 and 3
Draft Selection Criteria
1 | MWs of Resource Dependent on Need | Generation MW Column
2 | Load Sensitivity | Load Sensitive Column
3 | Appears in Previous Studies | Needs Results Columns
4 | Not in Base Reliability Plan | Confirm against CTPC Plan
5 | Multiple MVST Scenarios and Base Cases | Cases with Overloads Columns
6 | Major Component Limited | Major Component Limited Column
7 | Bulk Transmission | Branch Type Column
8 | Load Serving Entity Plan Alignment | Input from LSE Stakeholders

## DEC_Needs_Summary
Duke Energy Carolinas - MVST Needs - DRAFT
|  |  | Max Loading [%] | # of Cases with Overloads | [8 empty] | Contains Overloaded Cases |  | Does Overload Exceed Major Component Rating
Branch Identifier | Branch Name | Branch Type | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (9) | Major Component Limited
306003,306004,1 | AKENS BL | 230 kV Line | 176.9 | 5 | 5 | 5 | 2 | 0 | 0 | 7 | 5 | 5 | 3 | 6 | Yes
306003,306004,2 | AKENS WH | 230 kV Line | 176.9 | 5 | 5 | 5 | 2 | 0 | 0 | 7 | 5 | 5 | 3 | 6 | Yes
307005,309402,2 | ANDERSON TIE 02 TERT | 230/100/44 kV Transformer | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307051,307120,1 | WESTBROOK | 44 kV Line | 235 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | No
306738,306869,1 | ARCADIA BL | 100 kV Line | 126.9 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 2 | Yes
306560,306869,1 | ARCADIA BL | 100 kV Line | 120.9 | 0 | 0 | 1 | 0 | 3 | 3 | 0 | 3 | 4 | 2 | 3 | Yes
308573,308574,1 | ARCADIA WH | 100 kV Line | 134.6 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 3 | Yes
306560,308574,1 | ARCADIA WH | 100 kV Line | 119.8 | 0 | 1 | 1 | 0 | 3 | 3 | 0 | 4 | 4 | 2 | 4 | Yes
308573,309899,1 | ARCADIA WH | 100 kV Line | 99.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306975,308786,1 | ASHE ST BL | 100 kV Line | 138.8 | 5 | 4 | 5 | 0 | 0 | 0 | 5 | 4 | 5 | 3 | 6 | Yes
306975,307982,1 | ASHE ST BL | 100 kV Line | 132.4 | 5 | 4 | 5 | 0 | 0 | 0 | 5 | 4 | 5 | 3 | 6 | Yes
306029,309149,2 | CHAMPION BL | 100 kV Line | 228.7 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306852,307982,1 | ASHE ST BL | 100 kV Line | 127.2 | 5 | 4 | 5 | 0 | 0 | 0 | 5 | 4 | 5 | 3 | 6 | Yes
306852,306875,1 | ASHE ST WH | 100 kV Line | 128.5 | 4 | 5 | 5 | 0 | 0 | 0 | 4 | 5 | 5 | 3 | 6 | Yes
306655,309275,1 | COLLINS BL | 100 kV Line | 203.8 | 1 | 5 | 5 | 0 | 2 | 3 | 1 | 7 | 8 | 3 | 7 | Yes
307344,307355,1 | TUXEDO A | 44 kV Line | 176 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | No
306447,306475,1 | AVERY BL | 100 kV Line | 95.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307942,308794,Z1 | CLINTON TIE | 100 kV Breaker | 159 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | No
306447,308830,1 | AVERY WH | 100 kV Line | 96.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306286,308791,1 | AVON WH | 100 kV Line | 121.2 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306292,308791,1 | AVON WH | 100 kV Line | 120.8 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306251,306292,1 | AVON WH | 100 kV Line | 119.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306124,306195,1 | BAINBRIDGE BL | 100 kV Line | 173.9 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306124,306155,1 | BAINBRIDGE BL | 100 kV Line | 151 | 5 | 5 | 1 | 0 | 0 | 0 | 5 | 5 | 1 | 3 | 5 | Yes
306195,309295,1 | BAINBRIDGE WH | 100 kV Line | 162.9 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306155,309295,1 | BAINBRIDGE WH | 100 kV Line | 162.9 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306763,308027,1 | BANNERTOWN BL | 100 kV Line | 116 | 4 | 1 | 1 | 1 | 0 | 1 | 5 | 1 | 2 | 3 | 2 | Yes
306804,306835,1 | BANNERTOWN WH | 100 kV Line | 107.4 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
306329,306353,1 | CHESTER WH | 100 kV Line | 156.6 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | No
306725,306804,1 | BANNERTOWN WH | 100 kV Line | 99.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306574,306687,1 | BATTE BL | 100 kV Line | 103.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | Yes
306687,309284,1 | BATTE WH | 100 kV Line | 103.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | Yes
307613,308144,1 | BEAR CREEK | 44 kV Line | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306250,306286,1 | BEAVER BL | 100 kV Line | 137.7 | 4 | 4 | 3 | 0 | 0 | 0 | 4 | 4 | 3 | 3 | 3 | Yes
306093,306250,1 | BEAVER BL | 100 kV Line | 125.7 | 4 | 2 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 2 | 2 | Yes
306490,309286,1 | BEULAH WH | 100 kV Line | 153 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | No
306454,306490,1 | BEULAH BL | 100 kV Line | 152.9 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | No
307036,307378,1 | BELFAST | 44 kV Line | 141.4 | 4 | 4 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 2 | 4 | Yes
307094,307103,1 | BELFAST | 44 kV Line | 136.5 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 3 | Yes
306310,308478,1 | GLEN SPRINGS BL | 100 kV Line | 150.7 | 1 | 1 | 1 | 3 | 3 | 3 | 4 | 4 | 4 | 3 | 3 | Yes
308559,309823,1 | BELMONT WH | 100 kV Line | 97.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307015,309301,1 | BELTON TIE 01 | 100/44 kV Transformer | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306454,306472,1 | BEULAH BL | 100 kV Line | 168.2 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306242,309319,Z1 | BUSH RIVER TIE 100-115 High Side | 100 kV Breaker | 149.9 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | No
306472,309286,1 | BEULAH WH | 100 kV Line | 171.5 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306541,306542,1 | GOOSE CREEK BL | 230 kV Line | 147.8 | 4 | 4 | 5 | 0 | 0 | 0 | 4 | 4 | 5 | 3 | 6 | Yes
306022,306035,1 | BOND BL | 100 kV Line | 253.4 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306022,306035,2 | BOND WH | 100 kV Line | 253.4 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306013,308622,2 | BROADWAY BL | 100 kV Line | 274.4 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306013,308622,1 | BROADWAY WH | 100 kV Line | 274.4 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306843,306845,1 | MICHIE WH | 230 kV Line | 147.7 | 2 | 1 | 4 | 0 | 0 | 0 | 2 | 1 | 4 | 3 | 2 | No
306266,306286,1 | GLEN SPRINGS WH | 100 kV Line | 142.3 | 5 | 4 | 5 | 3 | 2 | 2 | 8 | 6 | 7 | 3 | 9 | No
306275,306560,1 | BUCK BL | 100 kV Line | 113.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | Yes
306275,308379,1 | BUCK BL | 100 kV Line | 113.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | Yes
306121,306183,1 | SEVIER BL | 100 kV Line | 142.2 | 5 | 5 | 4 | 0 | 0 | 0 | 5 | 5 | 4 | 3 | 5 | No
306453,309647,1 | HICKORY BL | 100 kV Line | 141.7 | 5 | 5 | 5 | 0 | 0 | 2 | 5 | 5 | 7 | 3 | 7 | Yes
306560,306561,1 | BUCK TIE - BUCK STEAM SEC 4 BUS RED | 100 kV Line | 140.1 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | Yes
306560,306561,2 | BUCK TIE - BUCK STEAM SEC 4 BUS YEL | 100 kV Line | 140.1 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | Yes
306687,308380,1 | buck wh | 100 kV Line | 154.9 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 4 | 5 | 2 | 3 | Yes
306563,308380,1 | buck wh | 100 kV Line | 147.1 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 4 | 5 | 2 | 3 | Yes
306560,306586,1 | BUCK WH | 100 kV Line | 97.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306563,306586,1 | BUCK WH | 100 kV Line | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306233,309404,1 | BUSH RIVER TIE 01 | 230/100/44 kV Transformer | 122.1 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | Yes
306286,308478,1 | GLEN SPRINGS BL | 100 kV Line | 139.9 | 4 | 2 | 4 | 3 | 2 | 3 | 7 | 4 | 7 | 3 | 6 | No
307035,309404,1 | BUSH RIVER TIE 01 TERT | 230/100/44 kV Transformer | 373.6 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306231,306242,6 | BUSH RIVER TIE 06 | 115/100 kV Transformer | 105.4 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | Yes
306232,309319,7 | BUSH RIVER TIE 07 | 115/100 kV Transformer | 198 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306232,309319,8 | BUSH RIVER TIE 08 | 115/100 kV Transformer | 171.9 | 5 | 4 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 2 | 4 | Yes
306066,307167,1 | TOXAWAY TIE 01 | 100/44 kV Transformer | 137.9 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | No
306017,306041,1 | CENTRAL WH | 100 kV Line | 137.6 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 3 | No
306681,306685,1 | CABARRUS BL | 100 kV Line | 180 | 5 | 5 | 5 | 1 | 1 | 1 | 6 | 6 | 6 | 3 | 6 | Yes
306681,308893,1 | CABARRUS WH | 100 kV Line | 110 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
307479,307481,1 | CAMPOBELLO A | 44 kV Line | 144.8 | 0 | 0 | 4 | 3 | 2 | 3 | 3 | 2 | 7 | 3 | 5 | Yes
307481,307518,1 | CAMPOBELLO A | 44 kV Line | 138.4 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 3 | 4 | Yes
307246,307518,1 | CAMPOBELLO A | 44 kV Line | 131.9 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | Yes
307411,307479,1 | CAMPOBELLO B | 44 kV Line | 108.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306160,306310,1 | GLEN SPRINGS WH | 100 kV Line | 136 | 1 | 1 | 2 | 3 | 2 | 2 | 4 | 3 | 4 | 3 | 4 | No
307478,307480,1 | CAMPOBELLO B | 44 kV Line | 99.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306664,306683,1 | CANAL BL | 100 kV Line | 117.4 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
306684,309941,1 | CANAL WH | 100 kV Line | 115.6 | 3 | 2 | 3 | 0 | 0 | 0 | 3 | 2 | 3 | 3 | 2 | Yes
306687,309963,1 | BUCK BL | 100 kV Line | 132.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
306417,308438,1 | CELRIVER WH | 100 kV Line | 96.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306041,306092,1 | CENTRAL BL | 100 kV Line | 121.1 | 4 | 2 | 1 | 0 | 0 | 0 | 4 | 2 | 1 | 3 | 3 | Yes
306948,306970,1 | RAM BL | 100 kV Line | 131.9 | 3 | 3 | 4 | 0 | 0 | 0 | 3 | 3 | 4 | 3 | 4 | No
306162,306183,1 | SEVIER WH | 100 kV Line | 131.9 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 3 | No
306112,306113,1 | WHITEWATER | 500 kV Line | 129.6 | 2 | 3 | 3 | 1 | 3 | 1 | 3 | 6 | 4 | 3 | 8 | No
306120,306163,1 | ECHO BL | 100 kV Line | 128.2 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | No
309406,309502,2 | CENTRAL TIE 02 | 230/100/44 kV Transformer | 98.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306004,309406,2 | CENTRAL TIE 02 | 230/100/44 kV Transformer | 98.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306004,309407,3 | CENTRAL TIE 03 | 230/100/44 kV Transformer | 95.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306063,306081,1 | WESTMINSTER WH | 100 kV Line | 128.2 | 3 | 3 | 3 | 1 | 1 | 1 | 4 | 4 | 4 | 3 | 3 | No
306242,309795,1 | CHAMPION BL | 100 kV Line | 281.5 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
306019,309795,1 | CHAMPION BL | 100 kV Line | 237.4 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
307452,307558,1 | SPINDALE | 44 kV Line | 128 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 1 | No
306019,309149,1 | CHAMPION BL | 100 kV Line | 164.7 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306242,308694,1 | CHAMPION WH | 100 kV Line | 149.1 | 4 | 4 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 2 | 2 | Yes
308694,309712,1 | CHAMPION WH | 100 kV Line | 122 | 4 | 4 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 2 | 2 | Yes
307035,307036,1 | CHAPPELLS | 44 kV Line | 180 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
307276,309376,1 | CHEROKEE WH | 100 kV Line | 136.2 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
308803,309376,1 | CHEROKEE WH | 100 kV Line | 136.1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 2 | Yes
308792,308803,1 | CHEROKEE WH | 100 kV Line | 135.2 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 2 | Yes
308792,309168,1 | CHEROKEE WH | 100 kV Line | 135 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 2 | Yes
306252,309168,1 | CHEROKEE WH | 100 kV Line | 134.7 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 2 | Yes
307425,309320,2 | CHESNEE TIE 02 | 100/44 kV Transformer | 139.8 | 1 | 0 | 1 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 3 | Yes
307425,309320,3 | CHESNEE TIE 03 | 100/44 kV Transformer | 141.4 | 1 | 0 | 1 | 3 | 3 | 3 | 4 | 3 | 4 | 3 | 3 | Yes
308786,309848,Z1 | ASHE ST BL | 100 kV Line | 127.4 | 5 | 4 | 5 | 0 | 0 | 0 | 5 | 4 | 5 | 3 | 6 | No
308729,308865,1 | BELMONT BL | 100 kV Line | 124.1 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | No
306001,339150,1 | CLARK HILL | 115 kV Line | 362.5 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 2 | Yes
307041,309302,1 | CLARK HILL TIE 01 | 100/44 kV Transformer | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307041,309302,2 | CLARK HILL TIE 02 | 100/44 kV Transformer | 170.6 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306001,306022,4 | CLARK HILL TIE 04 | 115/100 kV Transformer | 251.9 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 2 | Yes
306630,306677,1 | CLEAR CREEK BL | 100 kV Line | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306677,306686,1 | CLEAR CREEK BL | 100 kV Line | 99.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306630,308886,1 | CLEAR CREEK WH | 100 kV Line | 96.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306245,306313,1 | CLIFFSIDE WH | 100 kV Line | 98.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307989,309423,2 | LONGVIEW TIE 02 TERT | 230/100/44 kV Transformer | 123 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | No
307574,309350,Z1 | TAYLORSVILLE TIE | 100/44 kV - 100 kV Breaker | 121.7 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
307432,307942,1 | CLINTON TIE 01 | 100/44 kV Transformer | 298.2 | 5 | 1 | 1 | 2 | 0 | 0 | 7 | 1 | 1 | 3 | 4 | Yes
306218,306242,1 | CLINTON WH | 100 kV Line | 102.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306268,307447,1 | CLINTON WH | 100 kV Line | 98.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307721,307798,1 | CLOVER | 44 kV Line | 160.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
307721,307843,1 | CLOVER | 44 kV Line | 160.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
307748,307798,1 | CLOVER | 44 kV Line | 142.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
307655,307844,1 | CLOVER | 44 kV Line | 115.1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 3 | 3 | 3 | 2 | Yes
306624,308856,1 | ROCKY RIVER BL | 100 kV Line | 121.4 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 2 | No
309275,309276,1 | COLLINS BL | 100 kV Line | 201.3 | 0 | 4 | 5 | 0 | 2 | 3 | 0 | 6 | 8 | 2 | 4 | Yes
306566,309276,1 | COLLINS BL | 100 kV Line | 181.8 | 0 | 4 | 5 | 0 | 1 | 0 | 0 | 5 | 5 | 2 | 3 | Yes
306650,306655,1 | COLLINS WH | 100 kV Line | 223.8 | 2 | 5 | 5 | 0 | 3 | 3 | 2 | 8 | 8 | 3 | 7 | Yes
306528,306650,1 | COLLINS WH | 100 kV Line | 221.2 | 2 | 5 | 5 | 0 | 3 | 3 | 2 | 8 | 8 | 3 | 7 | Yes
306528,306671,1 | COLLINS WH | 100 kV Line | 187 | 0 | 4 | 5 | 0 | 1 | 0 | 0 | 5 | 5 | 2 | 3 | Yes
306566,306671,1 | COLLINS WH | 100 kV Line | 168 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 4 | 5 | 2 | 3 | Yes
306549,306557,1 | COMMONWEALTH WH | 100 kV Line | 110.4 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306573,309611,1 | CONCORD BL | 100 kV Line | 125.7 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
308132,309374,7 | CONCORD MAIN 07 | 100/44 kV Transformer | 110.2 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
308132,309374,8 | CONCORD MAIN 08 | 100/44 kV Transformer | 110.2 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
307094,307127,1 | COPELAND | 44 kV Line | 427 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
307127,307432,1 | COPELAND | 44 kV Line | 407.2 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306029,306046,1 | CORONACA | 100 kV Line | 107.2 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306046,307391,1 | CORONACA | 100 kV Line | 99.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306028,307049,2 | CORONACA TIE 02 | 100/44 kV Transformer | 125.5 | 0 | 4 | 5 | 1 | 2 | 2 | 1 | 6 | 7 | 3 | 5 | Yes
307005,307110,1 | GREGG | 44 kV Line | 121.2 | 3 | 3 | 3 | 1 | 1 | 1 | 4 | 4 | 4 | 3 | 3 | No
307790,309463,4 | SHELBY TIE 04 TERT | 230/100/44 kV Transformer | 121.1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | No
306190,308711,2 | RUGBY WH | 100 kV Line | 120.8 | 1 | 1 | 3 | 2 | 2 | 2 | 3 | 3 | 5 | 3 | 3 | No
307403,307590,1 | GASTON SHOALS | 44 kV Line | 120.7 | 3 | 3 | 4 | 1 | 1 | 1 | 4 | 4 | 5 | 3 | 4 | No
306030,307051,3 | CYPRESS TIE 03 | 100/44 kV Transformer | 104.8 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
308104,308455,1 | NESBIT BL | 100 kV Line | 120.7 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | No
306443,308142,5 | MARSHALL STEAM STA 05 | 230/44 kV Transformer | 120.2 | 0 | 3 | 3 | 1 | 1 | 0 | 1 | 4 | 3 | 3 | 2 | No
307989,308029,1 | DALE | 44 kV Line | 151 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | Yes
306164,306190,1 | RUGBY BL | 100 kV Line | 119.3 | 1 | 2 | 3 | 1 | 1 | 1 | 2 | 3 | 4 | 3 | 3 | No
306737,308923,1 | DAN RIVER BL | 100 kV Line | 99.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306958,308089,1 | DAN RIVER BL | 100 kV Line | 98.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306737,306810,1 | DAN RIVER WH | 100 kV Line | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306600,306601,1 | CRAB ORCHARD WH | 100 kV Line | 119.2 | 1 | 2 | 4 | 0 | 0 | 0 | 1 | 2 | 4 | 3 | 2 | No
306902,308930,1 | DEEP RIVER BL | 100 kV Line | 126.1 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 6 | Yes
306726,306805,1 | DEEP RIVER BL | 100 kV Line | 116.1 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
306805,306986,1 | DEEP RIVER BL | 100 kV Line | 116.1 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
306989,308930,1 | DEEP RIVER BL | 100 kV Line | 113 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306726,308922,1 | DEEP RIVER WH | 100 kV Line | 110 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306890,306902,1 | DEEP RIVER WH | 100 kV Line | 108.1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
308631,308994,1 | DELTA BL | 100 kV Line | 110.8 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 0 | Yes
306845,309548,1 | E DURHAM TIE 01 | 230/100 kV Transformer | 118.4 | 4 | 4 | 5 | 0 | 0 | 0 | 4 | 4 | 5 | 3 | 5 | No
306880,308631,Z1 | DELTA BL | 100 kV Line | 95.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306880,306952,1 | DELTA BL | 100 kV Line | 95.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308929,308940,1 | DELTA WH | 100 kV Line | 104.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | Yes
306788,306812,1 | DOZIER BL | 100 kV Line | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306629,308884,1 | DUNBAR WH | 100 kV Line | 99.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306674,308884,1 | DUNBAR WH | 100 kV Line | 97.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306248,307611,1 | DUNCAN BL | 100 kV Line | 121.1 | 2 | 3 | 3 | 0 | 0 | 0 | 2 | 3 | 3 | 3 | 2 | Yes
306028,307049,3 | CORONACA TIE 03 | 100/44 kV Transformer | 118 | 0 | 3 | 3 | 0 | 1 | 1 | 0 | 4 | 4 | 2 | 2 | No
306245,306248,1 | DUNCAN BL | 100 kV Line | 99.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306260,309889,1 | DUNCAN WH | 100 kV Line | 110.4 | 1 | 0 | 3 | 2 | 2 | 2 | 3 | 2 | 5 | 3 | 3 | Yes
306198,309889,1 | DUNCAN WH | 100 kV Line | 108.9 | 1 | 0 | 3 | 1 | 0 | 1 | 2 | 0 | 4 | 2 | 2 | Yes
306260,308795,1 | DUNCAN WH N | 100 kV Line | 129.5 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 4 | Yes
308494,308795,1 | DUNCAN WH N | 100 kV Line | 129.5 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 4 | Yes
308325,309430,3 | MITCHELL RIVER TIE 03 TERT | 230/100/44 kV Transformer | 117.5 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | No
306171,308740,1 | ECHO WH | 100 kV Line | 117.2 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 0 | No
306487,309647,1 | HICKORY WH | 100 kV Line | 117.2 | 1 | 1 | 5 | 0 | 0 | 0 | 1 | 1 | 5 | 3 | 2 | No
307933,308052,1 | OLD FORT | 44 kV Line | 116.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | No
308191,308235,1 | EAST RIVER | 44 kV Line | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306138,306144,1 | EASTOVER BL | 100 kV Line | 97.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306153,307000,1 | SEVIER WH | 100 kV Line | 116.9 | 4 | 1 | 3 | 0 | 0 | 0 | 4 | 1 | 3 | 3 | 2 | No
306164,308471,1 | ECHO BL | 100 kV Line | 126.9 | 1 | 1 | 3 | 2 | 2 | 2 | 3 | 3 | 5 | 3 | 4 | Yes
306164,308740,1 | ECHO WH | 100 kV Line | 117.3 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 0 | Yes
306041,308622,4 | STATES CTCC BUS LINE 4 | 100 kV Bus Line | 116.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306346,306376,1 | EDGEMOOR B&W NORTH | 100 kV Line | 142.6 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306369,306376,Z1 | EDGEMOOR B&W NORTH | 100 kV Line | 125.9 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
308689,308747,1 | EDGEMOOR B&W SOUTH | 100 kV Line | 132.8 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306369,308689,1 | EDGEMOOR B&W SOUTH | 100 kV Line | 132.8 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306375,308747,1 | EDGEMOOR B&W SOUTH | 100 kV Line | 116.1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
309645,309816,2 | BROOKFORD WH | 230 kV Line | 116.2 | 0 | 1 | 4 | 2 | 3 | 3 | 2 | 4 | 7 | 3 | 5 | No
306602,306631,1 | ELIZABETH WH | 100 kV Line | 115.1 | 2 | 1 | 3 | 0 | 0 | 0 | 2 | 1 | 3 | 3 | 1 | Yes
306838,306881,1 | ENO BL | 100 kV Line | 102.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
309413,309901,3 | ENO TIE 03 | 230/100/44 kV Transformer | 117 | 3 | 3 | 4 | 0 | 0 | 0 | 3 | 3 | 4 | 3 | 4 | Yes
309413,309585,3 | ENO TIE 03 | 230/100/44 kV Transformer | 110.5 | 2 | 2 | 4 | 0 | 0 | 0 | 2 | 2 | 4 | 3 | 2 | Yes
308422,309413,3 | ENO TIE 03 TERT | 230/100/44 kV Transformer | 134.2 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
309414,309900,4 | ENO TIE 04 | 230/100/44 kV Transformer | 121.2 | 3 | 3 | 4 | 0 | 0 | 0 | 3 | 3 | 4 | 3 | 4 | Yes
309414,309586,4 | ENO TIE 04 | 230/100/44 kV Transformer | 117.7 | 3 | 3 | 4 | 0 | 0 | 0 | 3 | 3 | 4 | 3 | 4 | Yes
306881,308777,1 | ENO WH | 100 kV Line | 109.8 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 1 | Yes
306740,306813,1 | FAIRPLAINS BL | 100 kV Line | 95.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306813,308636,1 | FAIRPLAINS WH | 100 kV Line | 95.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306198,308799,1 | DUNCAN BL | 100 kV Line | 116.2 | 0 | 0 | 0 | 2 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | No
306009,306066,2 | FIBER BL | 100 kV Line | 116.3 | 0 | 1 | 3 | 3 | 3 | 3 | 3 | 4 | 6 | 3 | 4 | Yes
306004,306104,1 | FISHER BL | 230 kV Line | 149.8 | 4 | 4 | 4 | 2 | 3 | 2 | 6 | 7 | 6 | 3 | 6 | Yes
306004,306105,2 | FISHER WH | 230 kV Line | 149.8 | 4 | 4 | 4 | 2 | 3 | 2 | 6 | 7 | 6 | 3 | 6 | Yes
306366,308254,1 | FISHING CREEK BL N | 100 kV Line | 98.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306380,308254,1 | FISHING CREEK BL N | 100 kV Line | 95.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306107,306111,1 | FLINT BL | 230 kV Line | 146 | 4 | 4 | 4 | 1 | 1 | 0 | 5 | 5 | 4 | 3 | 5 | Yes
306111,309819,2 | FLINT WH | 230 kV Line | 146 | 4 | 4 | 4 | 1 | 1 | 0 | 5 | 5 | 4 | 3 | 5 | Yes
307041,307062,1 | FLORIDA | 44 kV Line | 345.5 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
307062,307097,1 | FLORIDA | 44 kV Line | 275.7 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
307032,307097,1 | FLORIDA | 44 kV Line | 212.7 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306726,306802,1 | FRONTIS WH | 100 kV Line | 99.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306798,308098,1 | FRONTIS WH | 100 kV Line | 97.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307472,307488,1 | GAFFNEY | 44 kV Line | 122.7 | 3 | 3 | 4 | 1 | 1 | 1 | 4 | 4 | 5 | 3 | 4 | Yes
306254,307465,1 | GAFFNEY TIE 01 | 100/44 kV Transformer | 120.3 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 3 | 4 | Yes
306254,307465,2 | GAFFNEY TIE 02 | 100/44 kV Transformer | 115 | 0 | 0 | 1 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | Yes
308980,309257,2 | GALENOR BL | 100 kV Line | 96.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306491,309347,Z1 | STATESVILLE TIE | 100/44 kV - 100 kV Breaker | 115.3 | 1 | 2 | 3 | 0 | 0 | 0 | 1 | 2 | 3 | 3 | 1 | No
307280,307295,1 | KANUGA | 44 kV Line | 115.2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | No
306198,306307,1 | TIGER BL | 100 kV Line | 115.1 | 1 | 1 | 3 | 1 | 0 | 1 | 2 | 1 | 4 | 3 | 4 | No
306876,307968,1 | GEER WH | 100 kV Line | 142.4 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306947,307968,1 | GEER WH | 100 kV Line | 142.4 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306875,306947,1 | GEER WH | 100 kV Line | 117.3 | 3 | 1 | 4 | 0 | 0 | 0 | 3 | 1 | 4 | 3 | 3 | Yes
306949,308639,1 | GLEN RAVEN WH | 100 kV Line | 99.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306092,308699,1 | CENTRAL BL | 100 kV Line | 114.7 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 1 | No
307027,307154,1 | KEOWEE 44 | 44 kV Line | 114.4 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | No
308139,308190,1 | MT MOURNE | 44 kV Line | 114.3 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306600,308863,1 | CRAB ORCHARD BL | 100 kV Line | 113.7 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | No
306375,309708,1 | LANDSFORD WH | 100 kV Line | 113.3 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | No
306262,306305,1 | KNOLLWOOD WH | 100 kV Line | 112.9 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306845,309849,1 | MICHIE BL | 230 kV Line | 112.9 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1
306616,306641,1 | GRANTS CREEK WH | 100 kV Line | 116.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306180,306181,1 | GREENBRIAR BL | 100 kV Line | 118.8 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
306721,306763,1 | YADKIN BL | 100 kV Line | 112.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
308156,308184,1 | HUNTERSVILLE | 44 kV Line | 112.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
308762,308763,1 | GREENBRIAR WH | 100 kV Line | 134 | 4 | 3 | 4 | 0 | 0 | 0 | 4 | 3 | 4 | 3 | 3 | Yes
306103,308762,1 | GREENBRIAR WH | 100 kV Line | 134 | 4 | 3 | 4 | 0 | 0 | 0 | 4 | 3 | 4 | 3 | 3 | Yes
306103,306157,1 | GREENBRIAR WH | 100 kV Line | 125.3 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
306155,306200,1 | GREENVILLE BL | 100 kV Line | 95.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306052,308699,1 | CENTRAL BL | 100 kV Line | 112.2 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 1 | No
306155,306201,1 | GREENVILLE WH | 100 kV Line | 95.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306035,306036,1 | GREENWOOD BL | 100 kV Line | 178.1 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306036,306039,1 | GREENWOOD BL | 100 kV Line | 151 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306038,306039,1 | GREENWOOD BL | 100 kV Line | 130 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306035,306100,1 | GREENWOOD WH | 100 kV Line | 147.7 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306100,308721,1 | GREENWOOD WH | 100 kV Line | 138.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306038,308721,1 | GREENWOOD WH | 100 kV Line | 135.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306263,306286,1 | LAWSONS FORK BL EAST | 100 kV Line | 111.9 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 2 | No
306198,308709,2 | HARLEY BL | 100 kV Line | 137.9 | 2 | 2 | 4 | 3 | 3 | 3 | 5 | 5 | 7 | 3 | 5 | Yes
306132,308709,2 | HARLEY BL | 100 kV Line | 120.9 | 1 | 0 | 3 | 2 | 3 | 2 | 3 | 3 | 5 | 3 | 4 | Yes
306132,306198,1 | HARLEY WH | 100 kV Line | 134.9 | 1 | 2 | 4 | 3 | 3 | 3 | 4 | 5 | 7 | 3 | 5 | Yes
307010,309377,2 | WHETSTONE WH | 100 kV Line Radial | 111.8 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | No
307283,309312,3 | HENDERSONVILLE TIE 03 | 100/44 kV Transformer | 100.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | Yes
306453,306472,1 | HICKORY BL | 100 kV Line | 156.7 | 5 | 5 | 5 | 2 | 2 | 3 | 7 | 7 | 8 | 3 | 7 | Yes
306172,308759,1 | MAULDIN BL | 100 kV Line | 111.2 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | No
306472,306504,1 | HICKORY WH | 100 kV Line | 165.1 | 5 | 5 | 5 | 2 | 3 | 3 | 7 | 8 | 8 | 3 | 8 | Yes
306487,306504,1 | HICKORY WH | 100 kV Line | 134.1 | 4 | 5 | 5 | 0 | 0 | 0 | 4 | 5 | 5 | 3 | 6 | Yes
306007,306008,A1 | OCONEE 230KV SWITCHYARD AT1 | 500/230 kV Transformer | 110.8 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 3 | No
306013,306038,1 | HODGES BL | 100 kV Line | 187.9 | 5 | 5 | 1 | 0 | 0 | 0 | 5 | 5 | 1 | 3 | 5 | Yes
306013,306057,1 | HODGES WH | 100 kV Line | 201.8 | 5 | 5 | 4 | 0 | 0 | 0 | 5 | 5 | 4 | 3 | 5 | Yes
306038,306057,1 | HODGES WH | 100 kV Line | 154.3 | 5 | 2 | 0 | 0 | 0 | 0 | 5 | 2 | 0 | 2 | 3 | Yes
306132,307053,2 | HOGBACK BL | 100 kV Line | 106.7 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 2 | 0 | 2 | 2 | Yes
306164,308711,2 | RUGBY WH | 100 kV Line | 110.7 | 1 | 0 | 1 | 1 | 0 | 1 | 2 | 0 | 2 | 2 | 0 | No
306132,306163,1 | HOGBACK WH | 100 kV Line | 105.6 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
307432,307493,1 | HOOKER | 44 kV Line | 189.4 | 5 | 1 | 1 | 0 | 0 | 0 | 5 | 1 | 1 | 3 | 4 | Yes
307492,307493,1 | HOOKER | 44 kV Line | 172.3 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
307085,307492,1 | HOOKER | 44 kV Line | 171.9 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306712,306715,2 | HORSE GAP WH | 230 kV Line | 100.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | Yes
306101,309313,1 | HORSESHOE TIE 01 | 115/100 kV Transformer | 116.9 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
306327,306346,1 | HUCKLEBERRY BL | 100 kV Line | 121 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 2 | Yes
306327,306399,1 | HUCKLEBERRY BL | 100 kV Line | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308856,309782,1 | ROCKY RIVER BL | 100 kV Line | 109.8 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2
307943,308066,1 | STONY POINT | 44 kV Line | 109.7 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306681,306701,1 | LEMLEY WH | 100 kV Line | 109 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
306667,306668,1 | INDIAN TRAIL BL | 100 kV Line | 97.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308414,308879,1 | INDIAN TRAIL WH | 100 kV Line | 105.8 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | Yes
307479,309323,1 | INMAN TIE 01 | 100/44 kV Transformer | 108.2 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 1 | Yes
307479,309323,3 | INMAN TIE 03 | 100/44 kV Transformer | 96.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306007,306106,1 | JOCASSEE BL | 230 kV Line | 155.9 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 3 | Yes
306113,307690,1 | JOCASSEE TIE | 500/230 kV Transformer | 102.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
306007,306106,2 | JOCASSEE WH | 230 kV Line | 155.9 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 3 | Yes
306279,308466,1 | JORDAN | 100 kV Line | 136.2 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | Yes
307938,308466,1 | JORDAN | 100 kV Line | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | Yes
306503,308830,1 | AVERY WH | 100 kV Line | 108.8 | 1 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 3 | 2 | 1 | No
306113,309002,1 | KATOMA | 500 kV Line | 119.4 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 3 | Yes
306008,309002,Z1 | KATOMA | 500 kV Line | 109.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306448,306990,1 | KENNEDY BL | 100 kV Line | 122.3 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306448,309650,1 | KENNEDY BL | 100 kV Line | 114.6 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306130,308836,1 | PERRY WH | 100 kV Line | 108.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
307035,307191,1 | KINARD | 44 kV Line | 234.2 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
307094,307191,1 | KINARD | 44 kV Line | 174.8 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306305,307083,1 | KNOLLWOOD bl | 100 kV Line | 96.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306061,306168,1 | WESTMINSTER WH | 100 kV Line Radial | 108.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306928,306943,1 | LAKE JEANETTE BL | 100 kV Line | 108.3 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306943,308957,1 | LAKE JEANETTE WH | 100 kV Line | 108.4 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
309405,309501,1 | CENTRAL TIE 01 | 230/100/44 kV Transformer | 108.6 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 0 | No
306611,306649,1 | LAKEWOOD BL | 100 kV Line | 99.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306375,306408,1 | LANDSFORD BL | 100 kV Line | 148.9 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | Yes
306346,306408,1 | LANDSFORD BL | 100 kV Line | 143.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306346,309708,1 | LANDSFORD WH | 100 kV Line | 126.6 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306254,306324,1 | BEAVER WH | 100 kV Line | 108.4 | 1 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 1 | No
307503,309324,1 | LAURENS TIE 01 | 100/44 kV Transformer | 133 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
307503,309324,2 | LAURENS TIE 02 | 100/44 kV Transformer | 117.7 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
306251,306263,1 | LAWSONS FORK BL EAST | 100 kV Line | 131.5 | 5 | 1 | 1 | 0 | 0 | 0 | 5 | 1 | 1 | 3 | 4 | Yes
306333,306541,1 | SANDY RIDGE BL | 230 kV Line | 108.1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 0 | No
306269,306286,1 | LAWSONS FORK WH | 100 kV Line | 118.4 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 3 | Yes
306041,307583,2 | LEE BL | 100 kV Line | 109.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306195,307583,2 | LEE BL | 100 kV Line | 106.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306195,309273,3 | LEE WH | 100 kV Line | 119.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306041,309273,3 | LEE WH | 100 kV Line | 117.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306566,306585,1 | LEMLEY BL | 100 kV Line | 123 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | Yes
306585,306681,1 | LEMLEY BL | 100 kV Line | 110.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306566,308859,1 | LEMLEY WH | 100 kV Line | 124.3 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | Yes
306558,308379,1 | BUCK BL | 100 kV Line | 108 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
306701,308859,1 | LEMLEY WH | 100 kV Line | 108.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
304248,306542,1 | LILESVILLE BL | 230 kV Line | 203.3 | 5 | 5 | 5 | 1 | 0 | 2 | 6 | 5 | 7 | 3 | 6 | Yes
305049,306542,1 | LILESVILLE WH | 230 kV Line | 186 | 5 | 3 | 5 | 1 | 0 | 1 | 6 | 3 | 6 | 3 | 5 | Yes
307211,309308,3 | LIONS MOUNTAIN TIE #3 | 100/44 kV Transformer | 95.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306274,306281,1 | LOCKHART BL | 100 kV Line | 207.7 | 5 | 5 | 4 | 2 | 0 | 0 | 7 | 5 | 4 | 3 | 7 | Yes
306274,306282,1 | LOCKHART WH | 100 kV Line | 227.7 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
306558,309963,1 | BUCK BL | 100 kV Line | 107.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
307989,309424,3 | LONGVIEW TIE 03 TERT | 230/100/44 kV Transformer | 135 | 1 | 1 | 2 | 3 | 3 | 3 | 4 | 4 | 5 | 3 | 3 | Yes
307992,309343,2 | LOOKOUT TIE 02 | 100/44 kV Transformer | 97.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308312,309361,2 | MADISON TIE 02 | 100/44 kV Transformer | 110.3 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | Yes
308312,309361,3 | MADISON TIE 03 | 100/44 kV Transformer | 110.3 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | Yes
307411,307478,1 | CAMPOBELLO B | 44 kV Line | 107.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
309451,309514,2 | PISGAH TIE 02 | 230/100/44 kV Transformer | 107.9 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306216,308755,1 | MAULDIN BL | 100 kV Line | 171.3 | 5 | 5 | 5 | 2 | 2 | 1 | 7 | 7 | 6 | 3 | 8 | Yes
306172,306216,1 | MAULDIN BL | 100 kV Line | 155.9 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
307346,307374,1 | LAKESIDE | 44 kV Line | 107.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306133,308765,1 | MAULDIN BL | 100 kV Line | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308759,308765,1 | MAULDIN BL | 100 kV Line | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306157,308758,1 | MAULDIN WH | 100 kV Line | 162.6 | 5 | 5 | 5 | 1 | 0 | 0 | 6 | 5 | 5 | 3 | 6 | Yes
306173,308758,1 | MAULDIN WH | 100 kV Line | 137.7 | 5 | 5 | 4 | 0 | 0 | 0 | 5 | 5 | 4 | 3 | 5 | Yes
306173,306186,1 | MAULDIN WH | 100 kV Line | 116.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
308433,309368,1 | MEBANE TIE 01 | 100/44 kV Transformer | 101.8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
308433,309368,2 | MEBANE TIE 02 | 100/44 kV Transformer | 101.1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
308433,309368,3 | MEBANE TIE 03 | 100/44 kV Transformer | 101.8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
308433,309368,4 | MEBANE TIE 04 | 100/44 kV Transformer | 97.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306227,307881,1 | MIDWAY BL | 100 kV Line | 107.7 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 1 | 4 | 3 | 4 | No
306847,309849,1 | MICHIE BL | 230 kV Line | 102.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306332,308334,2 | PEACOCK BL | 230 kV Line | 107.3 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | No
306228,306281,1 | MIDWAY BL | 100 kV Line | 186.7 | 5 | 5 | 5 | 3 | 0 | 3 | 8 | 5 | 8 | 3 | 8 | Yes
306227,306242,1 | MIDWAY BL | 100 kV Line | 114.2 | 1 | 2 | 5 | 0 | 0 | 2 | 1 | 2 | 7 | 3 | 5 | Yes
306332,306334,1 | PEACOCK WH | 230 kV Line | 107.3 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | No
306228,307881,1 | MIDWAY BL | 100 kV Line | 95.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306282,306309,1 | MIDWAY WH | 100 kV Line | 162.4 | 5 | 5 | 5 | 1 | 0 | 3 | 6 | 5 | 8 | 3 | 7 | Yes
306242,306283,1 | MIDWAY WH | 100 kV Line | 139.5 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306283,306309,1 | MIDWAY WH | 100 kV Line | 128.7 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306226,306245,1 | DUNCAN WH N | 100 kV Line | 107 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306654,309296,Z1 | MONROE BL | 100 kV Line | 296 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
308874,309296,Z1 | MONROE WH | 100 kV Line | 346.1 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
306331,306332,2 | MOSER BL | 230 kV Line | 110.6 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
306331,306332,1 | MOSER WH | 230 kV Line | 110.6 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
306641,309297,1 | GRANTS CREEK BL | 100 kV Line | 107 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
306600,306617,1 | N CHARLOTTE BL | 100 kV Line | 122.2 | 4 | 3 | 5 | 0 | 0 | 0 | 4 | 3 | 5 | 3 | 5 | Yes
306617,306665,1 | N CHARLOTTE BL | 100 kV Line | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306600,308866,1 | N CHARLOTTE WH | 100 kV Line | 123.2 | 4 | 3 | 4 | 0 | 0 | 0 | 4 | 3 | 4 | 3 | 5 | Yes
306666,308866,1 | N CHARLOTTE WH | 100 kV Line | 114 | 1 | 3 | 3 | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 2 | Yes
309432,309523,1 | N GREENSBORO TIE 01 | 230/100/44 kV Transformer | 98.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306846,309432,1 | N GREENSBORO TIE 01 | 230/100/44 kV Transformer | 97.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306943,308436,5 | N GREENSBORO TIE 05 | 100/44 kV Transformer | 110.8 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | Yes
307085,307503,1 | NALLEY | 44 kV Line | 312.9 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306627,308853,1 | INDIAN TRAIL BL | 100 kV Line | 106.9 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306333,306337,A5 | NEWPORT TIE AT5 | 500/230 kV Transformer | 190.2 | 5 | 5 | 5 | 3 | 2 | 3 | 8 | 7 | 8 | 3 | 9 | Yes
307424,307748,1 | NINETY-NINE | 44 kV Line | 95.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306540,306543,1 | NORMAN BL | 230 kV Line | 115.4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | Yes
306540,308543,2 | NORMAN wh | 230 kV Line | 115.3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | Yes
306017,308752,1 | NORRIS BL | 100 kV Line | 99.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306002,306017,1 | NORRIS WH | 100 kV Line | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306689,309283,1 | OAKBORO BL | 100 kV Line | 105.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
309450,309513,1 | PISGAH TIE 01 | 230/100/44 kV Transformer | 106.9 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306845,309549,2 | E DURHAM TIE 02 | 230/100 kV Transformer | 106.3 | 2 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | 3 | 2 | 1 | No
306183,306195,1 | OAKVALE BL | 100 kV Line | 171.6 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | Yes
307328,309315,2 | OAKVALE TIE 02 | 100/44 kV Transformer | 132.2 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | Yes
306183,306195,2 | OAKVALE WH | 100 kV Line | 171.6 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | Yes
306163,309312,Z1 | HENDERSONVILLE TIE | 100/44 kV - 100 kV Breaker | 106.3 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306687,309285,1 | ODELL BL | 100 kV Line | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306570,306687,1 | ODELL WH | 100 kV Line | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307545,307621,1 | THICKETTY | 44 kV Line | 106.2 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306278,306286,1 | PACWAY BL | 100 kV Line | 229.6 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
306278,306281,1 | PACWAY BL | 100 kV Line | 146.3 | 5 | 1 | 3 | 0 | 0 | 0 | 5 | 1 | 3 | 3 | 5 | Yes
306286,308475,1 | PACWAY WH | 100 kV Line | 219.2 | 5 | 5 | 0 | 3 | 0 | 0 | 8 | 5 | 0 | 2 | 5 | Yes
308475,308905,1 | PACWAY WH | 100 kV Line | 196.5 | 5 | 4 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 2 | 4 | Yes
306282,308801,1 | PACWAY WH | 100 kV Line | 193.5 | 5 | 5 | 1 | 3 | 0 | 0 | 8 | 5 | 1 | 3 | 5 | Yes
308801,308905,1 | PACWAY WH | 100 kV Line | 171.2 | 5 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 2 | 4 | Yes
306333,370020,1 | PARR BL | 230 kV Line | 197.1 | 5 | 5 | 5 | 2 | 0 | 2 | 7 | 5 | 7 | 3 | 8 | Yes
306385,308244,1 | PARR WH | 100 kV Line | 139.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306353,309269,1 | PARR WH | 100 kV Line | 126.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306414,309269,1 | PARR WH | 100 kV Line | 122.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306111,306236,1 | PEACH VALLEY BL | 230 kV Line | 122.8 | 1 | 3 | 3 | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 2 | Yes
307542,309445,1 | PEACH VALLEY TIE 01 TERT | 230/100/44 kV Transformer | 105.3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | Yes
306111,306236,2 | PEACH VALLEY WH | 230 kV Line | 122.8 | 1 | 3 | 3 | 0 | 0 | 0 | 1 | 3 | 3 | 3 | 2 | Yes
307554,307621,1 | THICKETTY | 44 kV Line | 106.2 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306334,309448,1 | PEACOCK TIE 01 | 230/100/44 kV Transformer | 95.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307403,307472,1 | GASTON SHOALS | 44 kV Line | 106.1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 3 | 3 | 1 | No
307040,307319,1 | PENDLETON | 44 kV Line | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306041,308492,1 | PERRY BL | 100 kV Line | 167.4 | 5 | 5 | 5 | 1 | 0 | 0 | 6 | 5 | 5 | 3 | 6 | Yes
308492,308748,1 | PERRY BL | 100 kV Line | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306041,308715,1 | PERRY WH | 100 kV Line | 141.6 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
308715,308836,1 | PERRY WH | 100 kV Line | 135.1 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 6 | Yes
306157,308836,1 | PERRY WH | 100 kV Line | 112.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306106,308489,2 | SHULER BL | 230 kV Line | 105.8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306119,306188,1 | PICKENS BL | 100 kV Line | 105.8 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306041,306151,1 | PIEDMONT BL | 100 kV Line | 105.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306041,309787,1 | PIEDMONT WH | 100 kV Line | 113.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306195,309787,1 | PIEDMONT WH | 100 kV Line | 110.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306106,308489,1 | SHULER WH | 230 kV Line | 105.8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306755,306788,1 | PINNACLE BL | 100 kV Line | 97.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306788,308949,1 | PINNACLE WH | 100 kV Line | 96.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304803,306108,1 | PISGAH BL | 230 kV Line | 134.8 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 1 | Yes
308040,308142,1 | TERRELL | 44 kV Line | 105.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | No
306108,309450,1 | PISGAH TIE 01 | 230/100/44 kV Transformer | 98.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306003,307005,3 | ANDERSON TIE 03 | 230/44 kV Transformer | 105.4 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
309451,309822,2 | PISGAH TIE 02 | 230/100/44 kV Transformer | 95.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308437,309452,1 | PLEASANT GARDEN TIE 01 TERT | 230/100/44 kV Transformer | 104.4 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
306536,306544,1 | PROVIDENCE BL | 230 kV Line | 115.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306536,306544,2 | PROVIDENCE WH | 230 kV Line | 115.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306160,306266,1 | GLEN SPRINGS WH | 100 kV Line | 105.4 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 0 | No
306041,306097,1 | RABON BL | 100 kV Line | 148.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306268,308714,1 | RABON BL | 100 kV Line | 135.4 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306097,308714,1 | RABON BL | 100 kV Line | 131.2 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 2 | 3 | Yes
306041,309167,2 | RABON WH | 100 kV Line | 194.1 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306268,308497,2 | RABON WH | 100 kV Line | 149.9 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
308497,309167,2 | RABON WH | 100 kV Line | 142.7 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306138,306201,1 | GREENVILLE WH | 100 kV Line | 105.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | No
306915,306948,1 | RAM WH | 100 kV Line | 99.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306949,309892,1 | RANDLEMAN BL | 100 kV Line | 151.4 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306834,306935,1 | RANDLEMAN BL | 100 kV Line | 123.2 | 5 | 5 | 5 | 1 | 1 | 1 | 6 | 6 | 6 | 3 | 6 | Yes
306899,306955,1 | RANDLEMAN BL | 100 kV Line | 97.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306949,309893,1 | RANDLEMAN WH | 100 kV Line | 154.9 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306935,306942,1 | RANDLEMAN WH | 100 kV Line | 105.7 | 2 | 3 | 1 | 0 | 0 | 0 | 2 | 3 | 1 | 3 | 1 | Yes
307701,307727,1 | RED RIVER NO 1 | 44 kV Line | 101.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
307695,307701,1 | RED RIVER NO 2 | 44 kV Line | 120.8 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 1 | Yes
307688,307695,1 | RED RIVER NO 2 | 44 kV Line | 114 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306286,308796,1 | BEAVER WH | 100 kV Line | 105.1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306725,306825,1 | PINNACLE BL | 100 kV Line | 105.1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306737,306790,2 | REIDSVILLE BL | 100 kV Line | 138.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306737,306790,1 | REIDSVILLE WH | 100 kV Line | 138.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
308793,309814,1 | ROBB BL | 100 kV Line | 121.8 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 2 | 3 | Yes
306106,306110,1 | SHILOH WH | 230 kV Line | 105.1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | No
306256,308696,1 | VANDERBILT BL | 100 kV Line | 105 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | No
306437,306635,1 | ROCKY RIVER WH | 100 kV Line | 136.9 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 2 | 5 | 2 | 2 | Yes
306180,308726,1 | GREENBRIAR BL | 100 kV Line | 104.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
308726,308755,1 | GREENBRIAR BL | 100 kV Line | 104.7 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
308028,308029,1 | DALE | 44 kV Line | 104.4 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306560,306655,2 | SALISBURY BL | 100 kV Line | 203.4 | 2 | 5 | 5 | 0 | 2 | 2 | 2 | 7 | 7 | 3 | 7 | Yes
306560,306655,1 | SALISBURY WH | 100 kV Line | 209.7 | 2 | 5 | 5 | 0 | 2 | 2 | 2 | 7 | 7 | 3 | 7 | Yes
306163,307053,2 | HOGBACK BL | 100 kV Line | 104.3 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | No
306475,308839,1 | AVERY BL | 100 kV Line | 104.2 | 1 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 3 | 2 | 1 | No
306287,308703,1 | HYSTRON WH | 100 kV Line | 104.2 | 1 | 0 | 3 | 1 | 0 | 1 | 2 | 0 | 4 | 2 | 1 | No
307154,309305,1 | SENECA TIE 01 | 100/44 kV Transformer | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307154,309305,2 | SENECA TIE 02 | 100/44 kV Transformer | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306219,306225,1 | SEVIER BL | 100 kV Line | 165.4 | 5 | 5 | 5 | 1 | 0 | 1 | 6 | 5 | 6 | 3 | 7 | Yes
306007,306107,1 | DACUS BL | 230 kV Line | 104.1 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 1 | No
306121,306225,1 | SEVIER BL | 100 kV Line | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306007,309819,2 | DACUS WH | 230 kV Line | 104.1 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 1 | No
307148,307203,1 | SANDY SPRINGS | 44 kV Line | 104.1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306199,308697,1 | SEVIER WH | 100 kV Line | 109.3 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
307060,307203,1 | SANDY SPRINGS | 44 kV Line | 104.1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
307346,309460,2 | SHADY GROVE TIE 02 TERT | 230/100/44 kV Transformer | 116.4 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | Yes
307790,309462,3 | SHELBY TIE 03 TERT | 230/100/44 kV Transformer | 100.1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | Yes
306153,308697,1 | SEVIER WH | 100 kV Line | 104.1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306629,306681,1 | SHERRILL BL | 100 kV Line | 120.7 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 2 | Yes
306629,306681,2 | SHERRILL WH | 100 kV Line | 120.9 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 2 | Yes
306190,308761,1 | DAVIDSON RIVER BL | 100 kV Line | 103.9 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
306547,308373,1 | OAKBORO WH | 100 kV Line | 103.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
306052,308722,1 | CENTRAL BL | 100 kV Line | 103.6 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306814,308775,1 | SILAS WH | 100 kV Line | 97.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306687,308871,1 | SKYBROOK BL | 100 kV Line | 142.3 | 3 | 5 | 5 | 0 | 0 | 0 | 3 | 5 | 5 | 3 | 6 | Yes
308259,308871,1 | SKYBROOK BL | 100 kV Line | 117.1 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 3 | 4 | 2 | 3 | Yes
306642,306687,1 | SKYBROOK WH | 100 kV Line | 125.4 | 1 | 3 | 5 | 0 | 0 | 0 | 1 | 3 | 5 | 3 | 3 | Yes
308003,308004,1 | CATAWBA VALLEY | 44 kV Line Radial | 103.5 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | No
306620,308499,1 | SPRINGFIELD BL | 100 kV Line | 97.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306621,309750,1 | SPRINGFIELD WH | 100 kV Line | 97.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306041,308622,1 | STATES 1 | 100 kV Line | 116.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306469,306470,1 | ASPEN | 100 kV Line | 103.3 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306948,306952,1 | DELTA BL | 100 kV Line | 103.1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | No
306331,306545,2 | STEELBERRY BL | 230 kV Line | 96.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306331,306545,1 | STEELBERRY WH | 230 kV Line | 96.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306808,309853,1 | STOKES BL | 100 kV Line | 145.5 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 1 | Yes
306808,308642,1 | STOKES BL | 100 kV Line | 123.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306787,308642,1 | STOKES BL | 100 kV Line | 112.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306809,309853,1 | STOKES BL | 100 kV Line | 110.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Yes
306809,308773,1 | STOKES WH | 100 kV Line | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307214,307256,1 | QUEBEC | 44 kV Line | 102.3 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | No
308052,309348,2 | SUGAR HILL TIE 02 | 100/44 kV Transformer | 154.9 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Yes
308052,309348,3 | SUGAR HILL TIE 03 | 100/44 kV Transformer | 155.2 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Yes
306247,307942,Z1 | CLINTON TIE | 100 kV Breaker | 101.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
308448,309369,2 | SWEPSONVILLE TIE 02 | 100/44 kV Transformer | 129.9 | 0 | 0 | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 3 | 1 | Yes
308448,309369,3 | SWEPSONVILLE TIE 03 | 100/44 kV Transformer | 129.8 | 0 | 0 | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 3 | 1 | Yes
308055,309349,1 | TABLE ROCK TIE 01 | 100/44 kV Transformer | 99.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306328,306353,1 | CHESTER BL | 100 kV Line | 101.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | No
308055,309349,3 | TABLE ROCK TIE 03 | 100/44 kV Transformer | 108.6 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
309281,339001,1 | TALLASSEE WH | 100 kV Line | 222.6 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 1 | Yes
309281,309282,1 | TALLASSEE WH | 100 kV Line | 107.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | Yes
306138,306161,1 | TAYLORS BL | 100 kV Line | 128.1 | 4 | 4 | 5 | 0 | 0 | 0 | 4 | 4 | 5 | 3 | 4 | Yes
306198,306211,1 | TAYLORS BL | 100 kV Line | 111 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
306138,308757,1 | TAYLORS WH | 100 kV Line | 114.7 | 1 | 1 | 3 | 0 | 0 | 0 | 1 | 1 | 3 | 3 | 1 | Yes
306017,308723,1 | REFUGE | 100 kV Line | 101.7 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306198,306212,1 | TAYLORS WH | 100 kV Line | 95.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306080,308723,1 | REFUGE | 100 kV Line | 101.7 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | No
308066,309350,1 | TAYLORSVILLE TIE 01 | 100/44 kV Transformer | 217.5 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
308066,309350,2 | TAYLORSVILLE TIE 02 | 100/44 kV Transformer | 217.8 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
306592,308895,1 | SUNSET WH | 100 kV Line | 101.6 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | No
307400,307590,1 | GASTON SHOALS | 44 kV Line | 101.4 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | No
308055,309349,2 | TABLE ROCK TIE 02 | 100/44 kV Transformer | 101.3 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | No
308486,308515,3 | THORPE HYDRO BK 03 | 161/66 kV Transformer | 113.6 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
306305,306307,1 | TIGER BL | 100 kV Line | 142.9 | 2 | 3 | 4 | 2 | 3 | 2 | 4 | 6 | 6 | 3 | 5 | Yes
306635,309283,1 | OAKBORO BL | 100 kV Line | 101.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
307350,309467,5 | TIGER TIE 05 TERT | 230/100/44 kV Transformer | 117.2 | 1 | 2 | 2 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 2 | Yes
306305,308809,1 | TIGER WH | 100 kV Line | 136.7 | 3 | 4 | 4 | 0 | 0 | 0 | 3 | 4 | 4 | 3 | 4 | Yes
306198,306271,1 | TIGER WH | 100 kV Line | 135.7 | 3 | 3 | 4 | 3 | 3 | 3 | 6 | 6 | 7 | 3 | 6 | Yes
306271,308809,1 | TIGER WH | 100 kV Line | 96.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306681,308892,4 | TIMBER BL | 100 kV Line | 98.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306629,306681,3 | TIMBER WH | 100 kV Line | 98.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
307617,308622,2 | TOXAWAY BL | 100 kV Line | 205.4 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306066,307617,2 | TOXAWAY BL | 100 kV Line | 177 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306028,307049,4 | CORONACA TIE 04 | 100/44 kV Transformer | 100.9 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 2 | 0 | No
306066,307167,2 | TOXAWAY TIE 02 | 100/44 kV Transformer | 96.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308622,309811,1 | TOXAWAY WH | 100 kV Line | 212 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306066,309811,1 | TOXAWAY WH | 100 kV Line | 151.2 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
308487,308488,1 | TUCKASEGEE - WEBSTER | 161 kV Line | 96.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
308487,308489,2 | TUCKASEGEE TIE 02 | 230/161 kV Transformer | 109.8 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | Yes
308487,308489,3 | TUCKASEGEE TIE 03 | 230/161 kV Transformer | 109.7 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | Yes
307235,307246,1 | TURNER A | 44 kV Line | 130.1 | 4 | 3 | 3 | 2 | 2 | 2 | 6 | 5 | 5 | 3 | 5 | Yes
307235,307381,1 | TURNER A | 44 kV Line | 127.8 | 4 | 3 | 3 | 2 | 2 | 2 | 6 | 5 | 5 | 3 | 5 | Yes
307246,307341,1 | TURNER B | 44 kV Line | 126.4 | 4 | 3 | 2 | 2 | 2 | 2 | 6 | 5 | 4 | 3 | 5 | Yes
307246,307304,1 | TUXEDO A | 44 kV Line | 176.6 | 5 | 5 | 4 | 3 | 3 | 3 | 8 | 8 | 7 | 3 | 9 | Yes
306839,309848,1 | BUTNER BL | 100 kV Line | 100.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | No
307304,308583,1 | TUXEDO A | 44 kV Line | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 2 | Yes
308582,308583,1 | TUXEDO A | 44 kV Line | 119.7 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 2 | Yes
307246,307343,1 | TUXEDO B | 44 kV Line | 153.3 | 5 | 5 | 1 | 2 | 2 | 2 | 7 | 7 | 3 | 3 | 7 | Yes
307343,307598,1 | TUXEDO B | 44 kV Line | 152.5 | 5 | 5 | 1 | 2 | 2 | 2 | 7 | 7 | 3 | 3 | 7 | Yes
306182,308760,1 | UNION BL | 100 kV Line | 108.2 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 1 | Yes
306176,306182,1 | UNION WH | 100 kV Line | 98.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306251,308696,1 | VANDERBILT BL | 100 kV Line | 115.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306630,308578,1 | WEDDINGTON WH | 100 kV Line | 100.7 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306256,306305,1 | VANDERBILT BL | 100 kV Line | 95.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
309404,309522,1 | BUSH RIVER TIE 01 | 230/100/44 kV Transformer | 100.6 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | No
308181,308235,1 | EAST RIVER | 44 kV Line | 100.5 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
307177,309306,2 | WALHALLA TIE 02 | 100/44 kV Transformer | 135.1 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
307177,309306,3 | WALHALLA TIE 03 | 100/44 kV Transformer | 134.2 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
307177,309306,4 | WALHALLA TIE 04 | 100/44 kV Transformer | 139 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 6 | Yes
306809,308371,2 | WALNUT COVE TIE 02 | 100/44 kV Transformer | 138.1 | 1 | 1 | 1 | 3 | 3 | 3 | 4 | 4 | 4 | 3 | 3 | Yes
306375,309837,2 | WATEREE B&W | 100 kV Line | 277 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306416,309837,2 | WATEREE B&W | 100 kV Line | 276.4 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
304734,306416,1 | WATEREE PLANT #1 | 115/100 kV Transformer | 148.2 | 3 | 3 | 5 | 0 | 0 | 1 | 3 | 3 | 6 | 3 | 4 | Yes
304734,306416,2 | WATEREE PLANT #2 | 115/100 kV Transformer | 148.2 | 3 | 3 | 5 | 0 | 0 | 1 | 3 | 3 | 6 | 3 | 4 | Yes
307016,307131,1 | WATTS MILL | 44 kV Line | 118.4 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
308488,308555,2 | WEBSTER TIE BK 02 | 161/66 kV Transformer | 174 | 1 | 1 | 1 | 3 | 3 | 3 | 4 | 4 | 4 | 3 | 3 | Yes
306763,306835,1 | BANNERTOWN WH | 100 kV Line | 100.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | No
306187,306212,1 | TAYLORS WH | 100 kV Line | 100.4 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
307030,307206,1 | WALHALLA | 44 kV Line | 100.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306062,306078,1 | WESTMINSTER BL | 100 kV Line Radial | 200.1 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306078,309747,1 | WESTMINSTER BL | 100 kV Line Radial | 194.7 | 5 | 5 | 5 | 3 | 3 | 3 | 8 | 8 | 8 | 3 | 9 | Yes
306071,309747,1 | WESTMINSTER BL | 100 kV Line Radial | 176.1 | 5 | 5 | 5 | 2 | 2 | 2 | 7 | 7 | 7 | 3 | 9 | Yes
306017,307868,1 | WESTMINSTER BL | 100 kV Line Radial | 125.1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | Yes
306042,307868,1 | WESTMINSTER BL | 100 kV Line Radial | 124.7 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 3 | 0 | Yes
306042,306062,1 | WESTMINSTER BL | 100 kV Line Radial | 124.5 | 1 | 1 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 3 | 0 | Yes
306584,306631,1 | ELIZABETH BL | 100 kV Line | 100.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | No
306017,306168,1 | WESTMINSTER WH | 100 kV Line Radial | 108.9 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | Yes
307309,307322,1 | MARIETTA | 44 kV Line | 100.2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306061,306064,1 | WESTMINSTER WH | 100 kV Line Radial | 99.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306377,307010,1 | WHETSTONE BL | 100 kV Line | 120.3 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 0 | Yes
306377,309377,2 | WHETSTONE WH | 100 kV Line Radial | 165.4 | 5 | 4 | 5 | 3 | 3 | 3 | 8 | 7 | 8 | 3 | 9 | Yes
308181,308406,1 | WEST RIVER | 44 kV Line | 100.2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
307034,307206,1 | WALHALLA | 44 kV Line | 100.1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | No
306813,308374,3 | WILKES TIE 03 | 100/44 kV Transformer | 101 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
306813,308374,4 | WILKES TIE 04 | 100/44 kV Transformer | 101 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0 | Yes
308675,309829,1 | WILLOW | 44 kV Line | 125.3 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 2 | Yes
307709,309829,1 | WILLOW | 44 kV Line | 125.3 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 2 | 2 | Yes
307056,307134,1 | WILSON CREEK | 44 kV Line | 99.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306726,306800,1 | WINSTON BL | 100 kV Line | 98.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306737,306790,4 | WOLF CREEK BL | 100 kV Line | 138.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306737,306790,3 | WOLF CREEK WH | 100 kV Line | 138.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
306595,306690,1 | WYLIE BL | 100 kV Line | 97.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306417,306705,1 | WYLIE WH | 100 kV Line | 96.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
306600,308575,1 | FERREL BL | 100 kV Line | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No

## DEP_Needs_Summary
Duke Energy Progress - MVST Needs - DRAFT
|  |  | Max Overload [%] | Cases with Overloads |  |  | Cases with Overloads | [5 empty] | Contains Overloaded Cases |  | Does Overload Exceed Major Component Rating
Branch Lookup | Monitored Branch | Facility - Line or Station Name | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Major Component Limited
304800,304812,1 | 304800 ASHVLE115ETT 115 304812 ASHVCC1C115 115 1 | Asheville CC Plant - Asheville Plant 115kV East (OL330) | 100.72 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | Yes
304445,304451,1 | 304445 CHOCOWINITY 230 304451 GREENVILE TT 230 1 | Aurora SS - Greenville 230kV (OL068) | 163.15 | 23 | 20 | 24 | 5 | 5 | 5 | 28 | 25 | 29 | 3 | 26 | Yes
304449,304473,1 | 304449 EDWARDS TAP 230 304473 PA-WASHINTON 230 1 | Aurora SS - Greenville 230kV (OL068) | 162.09 | 25 | 22 | 25 | 7 | 5 | 10 | 32 | 27 | 35 | 3 | 30 | Yes
304445,304473,1 | 304445 CHOCOWINITY 230 304473 PA-WASHINTON 230 1 | Aurora SS - Greenville 230kV (OL068) | 152.43 | 20 | 15 | 18 | 4 | 3 | 5 | 24 | 18 | 23 | 3 | 20 | Yes
304449,304454,1 | 304449 EDWARDS TAP 230 304454 AURORA SS TT 230 1 | Aurora SS - Greenville 230kV (OL068) | 142.62 | 13 | 12 | 14 | 0 | 0 | 0 | 13 | 12 | 14 | 3 | 17 | Yes
304434,304454,1 | 304434 BAYBORO TAP 230 304454 AURORA SS TT 230 1 | Aurora SS - New Bern 230kV (OL003) | 153.81 | 23 | 19 | 23 | 3 | 3 | 3 | 26 | 22 | 26 | 3 | 24 | Yes
304463,304465,1 | 304463 NEW BERN WES 230 304465 NEWBERN230TT 230 1 | Aurora SS - New Bern 230kV (OL003) | 129.42 | 5 | 3 | 6 | 7 | 5 | 10 | 12 | 8 | 16 | 3 | 0 | Yes
304463,305142,1 | 304463 NEW BERN WES 230 305142 E16-FAIRFELD 230 1 | Aurora SS - New Bern 230kV (OL003) | 127.74 | 5 | 3 | 6 | 5 | 5 | 5 | 10 | 8 | 11 | 3 | 0 | Yes
304434,305142,1 | 304434 BAYBORO TAP 230 305142 E16-FAIRFELD 230 1 | Aurora SS - New Bern 230kV (OL003) | 125.77 | 5 | 3 | 5 | 5 | 4 | 5 | 10 | 7 | 10 | 3 | 0 | Yes
304342,339001,1 | 304342 BADIN #1 115 339001 BADIN 100 1 | Badin Transformer 115kV/100kV #1 | 180.86 | 21 | 6 | 25 | 10 | 0 | 6 | 31 | 6 | 31 | 3 | 23 | TBD
304343,339001,1 | 304343 BADIN #2 115 339001 BADIN 100 1 | Badin Transformer 115kV/100kV #2 | 172.31 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | TBD
304614,304619,1 | 304614 BARNCRK W TT 230 304619 MASONBORO 230 1 | Barnard Creek - Castle Hayne 230kV (OL355) | 110.2 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 2 | No
304619,304626,1 | 304619 MASONBORO 230 304626 WRIGHTSVILLE 230 1 | Barnard Creek - Castle Hayne 230kV (OL355) | 98.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304001,304004,1 | 304001 BLEWETT115TT 115 304004 TILLERY115TT 115 1 | Blewett Falls Plant - Tillery Plant 115kV (OL087) | 119.02 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | No
304022,305009,1 | 304022 BRUN1 230 TT 230 305009 E1-DAWSCREEK 230 1 | Brunswick Unit 1 - Barnard Creek 230kV (OL111) | 111.86 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 2 | Yes
304022,304610,1 | 304022 BRUN1 230 TT 230 304610 SPRT &PA TAP 230 1 | Brunswick Unit 1 - Delco 230kV East (OL127) | 120.8 | 11 | 9 | 8 | 3 | 3 | 3 | 14 | 12 | 11 | 3 | 9 | Yes
304610,305010,1 | 304610 SPRT &PA TAP 230 305010 E1-BOLIVIA 230 1 | Brunswick Unit 1 - Delco 230kV East (OL127) | 108.29 | 5 | 4 | 3 | 1 | 1 | 0 | 6 | 5 | 3 | 3 | 1 | Yes
304582,305010,1 | 304582 DELCO230 TT 230 305010 E1-BOLIVIA 230 1 | Brunswick Unit 1 - Delco 230kV East (OL127) | 96.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304022,305995,1 | 304022 BRUN1 230 TT 230 305995 6SUTNORTH230 230 1 | Brunswick Unit 1 - Jacksonville 230kV (OL129) | 170.94 | 4 | 5 | 5 | 1 | 1 | 1 | 5 | 6 | 6 | 3 | 0 | Yes
304022,304046,1 | 304022 BRUN1 230 TT 230 304046 WSPOON230 TT 230 1 | Brunswick Unit 1 - Weatherspoon Plant 230kV (OL135) | 142.78 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 6 | 6 | 3 | 0 | Yes
304020,305005,1 | 304020 BRUN2 230 TT 230 305005 E1-SOUTHPORT 230 1 | Brunswick Unit 2 - Delco 230kV West (OL142) | 114.48 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 0 | Yes
304582,305005,1 | 304582 DELCO230 TT 230 305005 E1-SOUTHPORT 230 1 | Brunswick Unit 2 - Delco 230kV West (OL142) | 100.89 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304020,305995,1 | 304020 BRUN2 230 TT 230 305995 6SUTNORTH230 230 1 | Brunswick Unit 2 - Wallace 230kV (OL143) | 193.89 | 5 | 5 | 5 | 4 | 4 | 7 | 9 | 9 | 12 | 3 | 0 | Yes
304515,305995,1 | 304515 WALLACE230TT 230 305995 6SUTNORTH230 230 1 | Brunswick Unit 2 - Wallace 230kV (OL143) | 154.74 | 5 | 5 | 5 | 7 | 7 | 5 | 12 | 12 | 10 | 3 | 0 | Yes
304020,305004,1 | 304020 BRUN2 230 TT 230 305004 E1-PROSPECT 230 1 | Brunswick Unit 2 - Whiteville 230kV (OL138) | 169.25 | 5 | 5 | 7 | 5 | 5 | 5 | 10 | 10 | 12 | 3 | 4 | Yes
305004,305011,1 | 305004 E1-PROSPECT 230 305011 ROYALOAK 230 1 | Brunswick Unit 2 - Whiteville 230kV (OL138) | 129.09 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304600,305011,1 | 304600 WHITEVL230TT 230 305011 ROYALOAK 230 1 | Brunswick Unit 2 - Whiteville 230kV (OL138) | 128.9 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304716,304725,1 | 304716 CAMDEN TAP 115 304725 CAMDEN115 TT 115 1 | Camden - Camden Junction 115kV (OL010) | 134.02 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | 2 | 10 | Yes
304716,304724,1 | 304716 CAMDEN TAP 115 304724 CAMD DEKALB 115 1 | Camden - Camden Junction 115kV (OL010) | 124.4 | 0 | 17 | 19 | 0 | 0 | 0 | 0 | 17 | 19 | 2 | 10 | Yes
304723,304726,1 | 304723 CAMDENJCT TT 115 304726 CAMDEN DUSTY 115 1 | Camden - Camden Junction 115kV (OL010) | 115.65 | 2 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 4 | 2 | 5 | Yes
304724,304738,1 | 304724 CAMD DEKALB 115 304738 CAMD KENDAL 115 1 | Camden - Camden Junction 115kV (OL010) | 110.44 | 0 | 10 | 9 | 0 | 0 | 0 | 0 | 10 | 9 | 2 | 9 | Yes
304726,304738,1 | 304726 CAMDEN DUSTY 115 304738 CAMD KENDAL 115 1 | Camden - Camden Junction 115kV (OL010) | 107.72 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 9 | 9 | 2 | 9 | Yes
304730,304725,1 | 304730 CAMDEN230 TT 230 304725 CAMDEN115 TT 115 1 | Camden 230kV | 124.46 | 0 | 9 | 18 | 0 | 0 | 0 | 0 | 9 | 18 | 2 | 9 | Yes
304731,304732,1 | 304731 CAMD DUP TT 115 304732 ELGIN TAP 115 1 | Camden DuPont - DPC Wateree Plant 115kV (OL126) | 235.87 | 24 | 25 | 25 | 6 | 6 | 20 | 30 | 31 | 45 | 3 | 35 | Yes
304732,304734,1 | 304732 ELGIN TAP 115 304734 WATEREE115TT 115 1 | Camden DuPont - DPC Wateree Plant 115kV (OL126) | 179.28 | 16 | 24 | 25 | 0 | 0 | 6 | 16 | 24 | 31 | 3 | 28 | Yes
304781,304780,1 | 304781 CANERV230 TT 230 304780 CANERV115STT 115 1 | Cane River 230kV | 105.25 | 0 | 0 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 3 | 0 | Yes
304208,304220,1 | 304208 ERWIN115 TT 115 304220 LILLINGTON 115 1 | Cape Fear Plant - Erwin 115kV (OL016) | 140.79 | 4 | 8 | 5 | 0 | 0 | 0 | 4 | 8 | 5 | 3 | 6 | Yes
304052,304220,1 | 304052 CAPEFR115STT 115 304220 LILLINGTON 115 1 | Cape Fear Plant - Erwin 115kV (OL016) | 110.02 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 2 | Yes
304513,304533,1 | 304513 BURGAW SUB 115 304533 INDUSTR TAP 115 1 | Castle Hayne - Wallace 115kV (OL023) | 128.35 | 3 | 3 | 0 | 5 | 5 | 5 | 8 | 8 | 5 | 3 | 0 | Yes
304533,304545,1 | 304533 INDUSTR TAP 115 304545 CASTLH115WTT 115 1 | Castle Hayne - Wallace 115kV (OL023) | 118.36 | 3 | 3 | 0 | 5 | 0 | 4 | 8 | 3 | 4 | 3 | 0 | Yes
304511,304513,1 | 304511 WALLACE TAP 115 304513 BURGAW SUB 115 1 | Castle Hayne - Wallace 115kV (OL023) | 103.78 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | Yes
304550,304545,1 | 304550 CASTLEH230TT 230 304545 CASTLH115WTT 115 1 | Castle Hayne 230kV | 109.72 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 0 | Yes
304170,304172,1 | 304170 CLAYTON 115 304172 CLAYTONINDTT 115 1 | Clayton Industrial - Milburnie 115kV (OL066) | 108.27 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
304175,304177,1 | 304175 SMITHF TAP 115 304177 SELMA 115 TT 115 1 | Clayton Industrial - Selma 115kV (OL319) | 140.85 | 19 | 13 | 19 | 0 | 0 | 0 | 19 | 13 | 19 | 3 | 18 | Yes
304172,304175,1 | 304172 CLAYTONINDTT 115 304175 SMITHF TAP 115 1 | Clayton Industrial - Selma 115kV (OL319) | 128.01 | 8 | 4 | 9 | 0 | 0 | 0 | 8 | 4 | 9 | 3 | 7 | Yes
304205,304218,1 | 304205 CLINTON230TT 230 304218 NEWTONGR TAP 230 1 | Clinton - Erwin 230kV (OL145) | 152.65 | 8 | 7 | 9 | 0 | 0 | 0 | 8 | 7 | 9 | 3 | 9 | Yes
304218,305122,1 | 304218 NEWTONGR TAP 230 305122 E15-BENSON 230 1 | Clinton - Erwin 230kV (OL145) | 150.96 | 6 | 6 | 8 | 0 | 0 | 0 | 6 | 6 | 8 | 3 | 9 | Yes
304197,305122,1 | 304197 DUNN 230 305122 E15-BENSON 230 1 | Clinton - Erwin 230kV (OL145) | 150.17 | 6 | 6 | 8 | 0 | 0 | 0 | 6 | 6 | 8 | 3 | 9 | Yes
304196,304197,1 | 304196 ERWIN230 TT 230 304197 DUNN 230 1 | Clinton - Erwin 230kV (OL145) | 144.21 | 5 | 5 | 8 | 0 | 0 | 0 | 5 | 5 | 8 | 3 | 7 | Yes
304266,305131,1 | 304266 FAISNHWYIND 115 305131 E15-HARGROVE 115 1 | Clinton - Mount Olive 115kV (OL303) | 126.19 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | 0 | Yes
304255,305131,1 | 304255 CLINTON115TT 115 305131 E15-HARGROVE 115 1 | Clinton - Mount Olive 115kV (OL303) | 120.23 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304266,304278,1 | 304266 FAISNHWYIND 115 304278 MT OLV115 TT 115 1 | Clinton - Mount Olive 115kV (OL303) | 109.96 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304255,305126,1 | 304255 CLINTON115TT 115 305126 E15-CLINTON 115 1 | Clinton - Vander 115kV (OL189) | 140.19 | 2 | 3 | 6 | 0 | 0 | 0 | 2 | 3 | 6 | 3 | 1 | Yes
304258,305126,1 | 304258 CLINTON NTH 115 305126 E15-CLINTON 115 1 | Clinton - Vander 115kV (OL189) | 135.95 | 1 | 1 | 6 | 0 | 0 | 0 | 1 | 1 | 6 | 3 | 1 | Yes
304258,305130,1 | 304258 CLINTON NTH 115 305130 E15-HALLPOND 115 1 | Clinton - Vander 115kV (OL189) | 123.42 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304260,305130,1 | 304260 ROSEBORO 115 305130 E15-HALLPOND 115 1 | Clinton - Vander 115kV (OL189) | 115.44 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304260,305133,1 | 304260 ROSEBORO 115 305133 E15-STEDMAN 115 1 | Clinton - Vander 115kV (OL189) | 107.41 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304401,305133,1 | 304401 VANDERSUB TT 115 305133 E15-STEDMAN 115 1 | Clinton - Vander 115kV (OL189) | 99.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304515,305031,1 | 304515 WALLACE230TT 230 305031 E4-BEVERAGE 230 1 | Clinton - Wallace 230kV (OL248) | 197.73 | 8 | 5 | 5 | 7 | 7 | 7 | 15 | 12 | 12 | 3 | 3 | Yes
304205,304503,1 | 304205 CLINTON230TT 230 304503 WARSAW TAP 230 1 | Clinton - Wallace 230kV (OL248) | 177.54 | 8 | 7 | 6 | 5 | 5 | 5 | 13 | 12 | 11 | 3 | 6 | Yes
304503,305032,1 | 304503 WARSAW TAP 230 305032 E4-BLIND BRG 230 1 | Clinton - Wallace 230kV (OL248) | 166.4 | 5 | 5 | 5 | 5 | 5 | 4 | 10 | 10 | 9 | 3 | 0 | Yes
304505,305032,1 | 304505 ROSE HILL 230 305032 E4-BLIND BRG 230 1 | Clinton - Wallace 230kV (OL248) | 142.44 | 5 | 5 | 3 | 5 | 5 | 4 | 10 | 10 | 7 | 3 | 0 | Yes
304505,305031,1 | 304505 ROSE HILL 230 305031 E4-BEVERAGE 230 1 | Clinton - Wallace 230kV (OL248) | 126.97 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304205,304255,1 | 304205 CLINTON230TT 230 304255 CLINTON115TT 115 1 | Clinton 230kV | 106.15 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | Yes
304390,305530,1 | 304390 CUMBLND230TT 230 305530 TRNBLSOLTAP 230 1 | Cumberland - Delco 230kV (OL141) | 189.83 | 8 | 8 | 8 | 0 | 0 | 0 | 8 | 8 | 8 | 3 | 9 | Yes
304584,305530,1 | 304584 GARLAND 230 305530 TRNBLSOLTAP 230 1 | Cumberland - Delco 230kV (OL141) | 186.12 | 8 | 8 | 8 | 0 | 0 | 0 | 8 | 8 | 8 | 3 | 9 | Yes
304584,305830,1 | 304584 GARLAND 230 305830 BAYTRESOLTAP 230 1 | Cumberland - Delco 230kV (OL141) | 170.76 | 8 | 7 | 7 | 0 | 0 | 3 | 8 | 7 | 10 | 3 | 7 | Yes
305830,900005,1 | 305830 BAYTRESOLTAP 230 900005 ID_564510 230 1 | Cumberland - Delco 230kV (OL141) | 164.83 | 5 | 4 | 5 | 0 | 3 | 3 | 5 | 7 | 8 | 3 | 0 | Yes
305390,900005,1 | 305390 ROWANSOL-TAP 230 900005 ID_564510 230 1 | Cumberland - Delco 230kV (OL141) | 157.14 | 3 | 3 | 4 | 0 | 3 | 3 | 3 | 6 | 7 | 3 | 0 | Yes
304582,305033,1 | 304582 DELCO230 TT 230 305033 E4-KELLY 230 1 | Cumberland - Delco 230kV (OL141) | 150.62 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 0 | Yes
305033,305390,1 | 305033 E4-KELLY 230 305390 ROWANSOL-TAP 230 1 | Cumberland - Delco 230kV (OL141) | 145.57 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 6 | 6 | 3 | 0 | Yes
304387,304390,2 | 304387 FAY 230 TT 230 304390 CUMBLND230TT 230 2 | Cumberland - Fayetteville 230kV South (OL199) | 107.1 | 2 | 2 | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 3 | 0 | Yes
305034,305330,1 | 305034 E4-POWELL 230 305330 BLADENSOLTAP 230 1 | Cumberland - Whiteville 230kV (OL247) | 121.12 | 4 | 2 | 2 | 0 | 0 | 0 | 4 | 2 | 2 | 3 | 1 | Yes
304600,305330,1 | 304600 WHITEVL230TT 230 305330 BLADENSOLTAP 230 1 | Cumberland - Whiteville 230kV (OL247) | 110.34 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 0 | Yes
305034,305035,1 | 305034 E4-POWELL 230 305035 E4-TARHELL 230 1 | Cumberland - Whiteville 230kV (OL247) | 108.19 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
304390,305035,1 | 304390 CUMBLND230TT 230 305035 E4-TARHELL 230 1 | Cumberland - Whiteville 230kV (OL247) | 101.01 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
304575,304587,1 | 304575 LAKE WACCA 115 304587 DELCO115W TT 115 1 | Delco - Whiteville 115kV (OL184) | 194.3 | 4 | 5 | 8 | 3 | 4 | 5 | 7 | 9 | 13 | 3 | 2 | Yes
304575,305003,1 | 304575 LAKE WACCA 115 305003 E1-HALLSBORO 115 1 | Delco - Whiteville 115kV (OL184) | 189.07 | 3 | 4 | 6 | 3 | 3 | 5 | 6 | 7 | 11 | 3 | 1 | Yes
304580,305003,1 | 304580 E1WHITVLTAP 115 305003 E1-HALLSBORO 115 1 | Delco - Whiteville 115kV (OL184) | 188.06 | 7 | 8 | 6 | 3 | 3 | 4 | 10 | 11 | 10 | 3 | 6 | Yes
304580,304581,1 | 304580 E1WHITVLTAP 115 304581 WHITEVL115TT 115 1 | Delco - Whiteville 115kV (OL184) | 107.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | No
304582,304587,1 | 304582 DELCO230 TT 230 304587 DELCO115W TT 115 1 | Delco 230kV | 182.26 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304582,304583,2 | 304582 DELCO230 TT 230 304583 DELCO115E TT 115 2 | Delco 230kV | 156.84 | 4 | 5 | 5 | 5 | 5 | 6 | 9 | 10 | 11 | 3 | 0 | Yes
304583,304587,Z1 | 304583 DELCO115E TT 115 304587 DELCO115W TT 115 Z1 | Delco 230kV | 96.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304187,304192,1 | 304187 PA-SMTHFLD2 230 304192 SELMA 230 TT 230 1 | Erwin - Selma 230kV (OL029) | 122.21 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304187,304193,1 | 304187 PA-SMTHFLD2 230 304193 FOUR OAKS 230 1 | Erwin - Selma 230kV (OL029) | 120.93 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304193,304259,1 | 304193 FOUR OAKS 230 304259 CLV MAT TAP 230 1 | Erwin - Selma 230kV (OL029) | 116.97 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | Yes
304194,304259,1 | 304194 BENSON 230 304259 CLV MAT TAP 230 1 | Erwin - Selma 230kV (OL029) | 109.19 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
304194,304217,1 | 304194 BENSON 230 304217 BENPGI TAP 230 1 | Erwin - Selma 230kV (OL029) | 102.93 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304196,304217,1 | 304196 ERWIN230 TT 230 304217 BENPGI TAP 230 1 | Erwin - Selma 230kV (OL029) | 100.47 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304096,304105,1 | 304096 YOUNGSVILLE 115 304105 FRANKLIN TT 115 1 | Falls - Franklinton 115kV East (OL042) | 103.51 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | Yes
304105,305173,1 | 304105 FRANKLIN TT 115 305173 E18-POCOMOKE 115 1 | Falls - Franklinton 115kV West (OL159) | 116.33 | 5 | 7 | 5 | 0 | 0 | 0 | 5 | 7 | 5 | 3 | 16 | Yes
305173,305176,1 | 305173 E18-POCOMOKE 115 305176 E18-YOUNGSVL 115 1 | Falls - Franklinton 115kV West (OL159) | 104.95 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 2 | 4 | Yes
305174,305176,1 | 305174 E18-WAKE FOR 115 305176 E18-YOUNGSVL 115 1 | Falls - Franklinton 115kV West (OL159) | 99.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304662,304707,2 | 304662 FLO SUB230TT 230 304707 FLOSUB115ETT 115 2 | Florence 230kV | 132.06 | 10 | 11 | 9 | 13 | 15 | 13 | 23 | 26 | 22 | 3 | 32 | No
304662,304659,1 | 304662 FLO SUB230TT 230 304659 FLOSUB115WTT 115 1 | Florence 230kV | 128.61 | 7 | 14 | 11 | 14 | 16 | 14 | 21 | 30 | 25 | 3 | 32 | No
304659,304707,Z1 | 304659 FLOSUB115WTT 115 304707 FLOSUB115ETT 115 Z1 | Florence 230kV | 122.45 | 3 | 7 | 2 | 8 | 15 | 13 | 11 | 22 | 15 | 3 | 23 | No
305169,305172,1 | 305169 LOUISBUR CAP 115 305172 E18-LOUISBRG 115 1 | Franklinton - Spring Hope SS 115kV (OL041) | 109.35 | 5 | 2 | 2 | 0 | 0 | 0 | 5 | 2 | 2 | 3 | 9 | Yes
304108,305660,1 | 304108 LOUISBURG 115 305660 FOXCRKSOLTAP 115 1 | Franklinton - Spring Hope SS 115kV (OL041) | 104.75 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 6 | Yes
304108,305169,1 | 304108 LOUISBURG 115 305169 LOUISBUR CAP 115 1 | Franklinton - Spring Hope SS 115kV (OL041) | 103.04 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 4 | Yes
304084,305172,1 | 304084 NOVOZYMES 115 305172 E18-LOUISBRG 115 1 | Franklinton - Spring Hope SS 115kV (OL041) | 102.18 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | Yes
304287,305052,1 | 304287 GOLDSB SSWTT 115 305052 E13-ARBA 115 1 | Goldsboro SS - Kinston DuPont 115kV (OL188) | 151.77 | 6 | 6 | 5 | 0 | 0 | 0 | 6 | 6 | 5 | 3 | 15 | Yes
304480,304481,1 | 304480 KINSDUP115TT 115 304481 PA-AYDEN 115 1 | Goldsboro SS - Kinston DuPont 115kV (OL188) | 106.1 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | Yes
304459,304481,1 | 304459 GRIFTON 115 304481 PA-AYDEN 115 1 | Goldsboro SS - Kinston DuPont 115kV (OL188) | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304286,304288,1 | 304286 GOLDSB SSETT 115 304288 LAGRANGE 115 1 | Goldsboro SS - Wommack 115kV (OL057) | 145.95 | 12 | 10 | 10 | 0 | 0 | 0 | 12 | 10 | 10 | 3 | 16 | Yes
304509,305159,1 | 304509 PA-KIN FALL 115 305159 E17-LAGRANGE 115 1 | Goldsboro SS - Wommack 115kV (OL057) | 145.17 | 15 | 12 | 11 | 0 | 0 | 0 | 15 | 12 | 11 | 3 | 18 | Yes
304288,305159,1 | 304288 LAGRANGE 115 305159 E17-LAGRANGE 115 1 | Goldsboro SS - Wommack 115kV (OL057) | 141.75 | 13 | 11 | 10 | 0 | 0 | 0 | 13 | 11 | 10 | 3 | 16 | Yes
304510,305153,1 | 304510 WOMACKW115TT 115 305153 E17-FALL CRK 115 1 | Goldsboro SS - Wommack 115kV (OL057) | 137.55 | 12 | 7 | 8 | 3 | 4 | 0 | 15 | 11 | 8 | 3 | 11 | Yes
304509,305153,1 | 304509 PA-KIN FALL 115 305153 E17-FALL CRK 115 1 | Goldsboro SS - Wommack 115kV (OL057) | 135.9 | 11 | 7 | 6 | 0 | 0 | 0 | 11 | 7 | 6 | 3 | 10 | Yes
304484,305018,1 | 304484 HAVELOK230TT 230 305018 E2-MAYSVILLE 230 1 | Grants Creek - Havelock 230kV (OL149) | 119.14 | 9 | 9 | 10 | 2 | 5 | 1 | 11 | 14 | 11 | 3 | 23 | Yes
304527,305018,1 | 304527 SWANSBORO 230 305018 E2-MAYSVILLE 230 1 | Grants Creek - Havelock 230kV (OL149) | 112.53 | 2 | 5 | 6 | 0 | 0 | 0 | 2 | 5 | 6 | 3 | 9 | Yes
304518,304527,1 | 304518 GRNTSCK230TT 230 304527 SWANSBORO 230 1 | Grants Creek - Havelock 230kV (OL149) | 112.33 | 2 | 2 | 4 | 0 | 0 | 0 | 2 | 2 | 4 | 3 | 7 | Yes
304451,314574,1 | 304451 GREENVILE TT 230 314574 6EVERETS 230 1 | Greenville - VP Everetts 230kV (OL243) | 108.94 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 3 | No
304451,304452,1 | 304451 GREENVILE TT 230 304452 GREENVILE W 230 1 | Greenville - Wilson 230kV (OL185) | 106.88 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 1 | Yes
304229,304289,1 | 304229 PA-FARMVILLE 230 304289 FARMVILLE 230 1 | Greenville - Wilson 230kV (OL185) | 103.24 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | Yes
304228,304229,1 | 304228 WILSON230 TT 230 304229 PA-FARMVILLE 230 1 | Greenville - Wilson 230kV (OL185) | 100.89 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | Yes
304466,304467,1 | 304466 NEWBER115NTT 115 304467 AMITAL TAP 115 1 | Havelock - New Bern 115kV (OL070) | 131.94 | 17 | 19 | 20 | 6 | 7 | 2 | 23 | 26 | 22 | 3 | 34 | Yes
304460,304467,1 | 304460 PA-NBLFRDTAP 115 304467 AMITAL TAP 115 1 | Havelock - New Bern 115kV (OL070) | 117.7 | 9 | 10 | 11 | 2 | 5 | 2 | 11 | 15 | 13 | 3 | 14 | Yes
304460,304485,1 | 304460 PA-NBLFRDTAP 115 304485 HAVLOK115NTT 115 1 | Havelock - New Bern 115kV (OL070) | 110.59 | 5 | 6 | 6 | 2 | 2 | 0 | 7 | 8 | 6 | 3 | 11 | Yes
304465,304484,1 | 304465 NEWBERN230TT 230 304484 HAVELOK230TT 230 1 | Havelock - New Bern 230kV (OL186) | 180.91 | 23 | 25 | 25 | 13 | 16 | 14 | 36 | 41 | 39 | 3 | 50 | Yes
304088,304089,2 | 304088 HENDER 230TT 230 304089 HENDER 115TT 115 2 | Henderson 230kV | 109.35 | 0 | 0 | 0 | 0 | 9 | 13 | 0 | 9 | 13 | 2 | 14 | No
304088,304089,1 | 304088 HENDER 230TT 230 304089 HENDER 115TT 115 1 | Henderson 230kV | 101.04 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 4 | 3 | 2 | 0 | No
305076,305077,1 | 305076 E9-HORACE 230 305077 E9-RAMSEY RD 230 1 | Jacksonville - New Bern 230kV (OL114) | 175.08 | 20 | 20 | 20 | 7 | 9 | 6 | 27 | 29 | 26 | 3 | 47 | Yes
304524,305077,1 | 304524 JACKSON230TT 230 305077 E9-RAMSEY RD 230 1 | Jacksonville - New Bern 230kV (OL114) | 172.97 | 20 | 20 | 20 | 7 | 9 | 2 | 27 | 29 | 22 | 3 | 43 | Yes
305076,305540,1 | 305076 E9-HORACE 230 305540 TRENTRSOLTAP 230 1 | Jacksonville - New Bern 230kV (OL114) | 140.21 | 16 | 20 | 20 | 7 | 8 | 6 | 23 | 28 | 26 | 3 | 44 | Yes
304471,304528,1 | 304471 CC WD EN TAP 230 304528 RHEMS 230 1 | Jacksonville - New Bern 230kV (OL114) | 135.7 | 12 | 14 | 20 | 7 | 9 | 7 | 19 | 23 | 27 | 3 | 42 | Yes
304528,305540,1 | 304528 RHEMS 230 305540 TRENTRSOLTAP 230 1 | Jacksonville - New Bern 230kV (OL114) | 132.76 | 11 | 13 | 20 | 7 | 8 | 6 | 18 | 21 | 26 | 3 | 36 | Yes
304465,304471,1 | 304465 NEWBERN230TT 230 304471 CC WD EN TAP 230 1 | Jacksonville - New Bern 230kV (OL114) | 132.03 | 6 | 10 | 15 | 7 | 8 | 6 | 13 | 18 | 21 | 3 | 30 | Yes
304525,305065,1 | 304525 JACKSN115ETT 115 305065 E9-GUMBRNCH 115 1 | Jacksonville - Wommack 115kV (OL109) | 144.17 | 5 | 5 | 3 | 0 | 0 | 0 | 5 | 5 | 3 | 3 | 0 | Yes
304507,305072,1 | 304507 WOMACKE115TT 115 305072 E9-PLEASANT 115 1 | Jacksonville - Wommack 115kV (OL109) | 142.82 | 5 | 3 | 3 | 0 | 0 | 0 | 5 | 3 | 3 | 3 | 0 | Yes
305062,305079,1 | 305062 E9-EAGLE NST 115 305079 E9-FRANTOWN 115 1 | Jacksonville - Wommack 115kV (OL109) | 141.67 | 5 | 5 | 3 | 0 | 0 | 0 | 5 | 5 | 3 | 3 | 0 | Yes
305065,305079,1 | 305065 E9-GUMBRNCH 115 305079 E9-FRANTOWN 115 1 | Jacksonville - Wommack 115kV (OL109) | 133.01 | 3 | 3 | 1 | 0 | 0 | 0 | 3 | 3 | 1 | 3 | 0 | Yes
305062,305080,1 | 305062 E9-EAGLE NST 115 305080 E9-ELMGROVE 115 1 | Jacksonville - Wommack 115kV (OL109) | 129.18 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | Yes
305072,305080,1 | 305072 E9-PLEASANT 115 305080 E9-ELMGROVE 115 1 | Jacksonville - Wommack 115kV (OL109) | 124.15 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | Yes
304477,304480,1 | 304477 VOA TAP 115 304480 KINSDUP115TT 115 1 | Kinston DuPont - New Bern 115kV (OL193) | 228.75 | 25 | 25 | 25 | 12 | 13 | 12 | 37 | 38 | 37 | 3 | 45 | Yes
304475,304477,1 | 304475 WEYER TAP 115 304477 VOA TAP 115 1 | Kinston DuPont - New Bern 115kV (OL193) | 199.67 | 25 | 25 | 25 | 12 | 13 | 13 | 37 | 38 | 38 | 3 | 47 | Yes
304466,304475,1 | 304466 NEWBER115NTT 115 304475 WEYER TAP 115 1 | Kinston DuPont - New Bern 115kV (OL193) | 196.62 | 25 | 25 | 25 | 11 | 11 | 12 | 36 | 36 | 37 | 3 | 43 | Yes
304179,304251,1 | 304179 WILSON MILLS 230 304251 LEESUB230 TT 230 1 | Lee - Milburnie 230kV (OL065) | 187.81 | 20 | 15 | 21 | 0 | 0 | 4 | 20 | 15 | 25 | 3 | 21 | Yes
304179,304239,1 | 304179 WILSON MILLS 230 304239 POW_IND_TAP 230 1 | Lee - Milburnie 230kV (OL065) | 181.18 | 17 | 14 | 20 | 0 | 0 | 3 | 17 | 14 | 23 | 3 | 18 | Yes
304239,304482,1 | 304239 POW_IND_TAP 230 304482 PA-CLAYNSID 230 1 | Lee - Milburnie 230kV (OL065) | 163.5 | 11 | 6 | 12 | 0 | 0 | 0 | 11 | 6 | 12 | 3 | 11 | Yes
304178,304482,1 | 304178 AUBURN 230 304482 PA-CLAYNSID 230 1 | Lee - Milburnie 230kV (OL065) | 159.08 | 7 | 5 | 11 | 0 | 0 | 0 | 7 | 5 | 11 | 3 | 9 | Yes
304162,304178,1 | 304162 MILBUR230 TT 230 304178 AUBURN 230 1 | Lee - Milburnie 230kV (OL065) | 156.83 | 7 | 4 | 10 | 0 | 0 | 0 | 7 | 4 | 10 | 3 | 8 | Yes
304192,304251,1 | 304192 SELMA 230 TT 230 304251 LEESUB230 TT 230 1 | Lee - Selma 230kV (OL055) | 170.67 | 14 | 8 | 18 | 0 | 0 | 8 | 14 | 8 | 26 | 3 | 14 | Yes
304271,304273,1 | 304271 FRNDSHIP TAP 115 304273 KORNEGAY SUB 115 1 | Lee - Wallace 115kV (OL056) | 148.57 | 8 | 3 | 3 | 0 | 0 | 0 | 8 | 3 | 3 | 3 | 3 | Yes
304261,304271,1 | 304261 LEESUB115STT 115 304271 FRNDSHIP TAP 115 1 | Lee - Wallace 115kV (OL056) | 142.88 | 7 | 3 | 3 | 0 | 0 | 0 | 7 | 3 | 3 | 3 | 2 | Yes
304280,305151,1 | 304280 BEULAVILLE 115 305151 E17-BEULAVIL 115 1 | Lee - Wallace 115kV (OL056) | 134.4 | 3 | 3 | 2 | 0 | 0 | 0 | 3 | 3 | 2 | 3 | 0 | Yes
304280,304517,1 | 304280 BEULAVILLE 115 304517 WALLACE115TT 115 1 | Lee - Wallace 115kV (OL056) | 132.42 | 3 | 3 | 1 | 4 | 0 | 0 | 7 | 3 | 1 | 3 | 0 | Yes
305151,305161,1 | 305151 E17-BEULAVIL 115 305161 E17-TAPPFARM 115 1 | Lee - Wallace 115kV (OL056) | 131.89 | 3 | 3 | 1 | 0 | 0 | 0 | 3 | 3 | 1 | 3 | 0 | Yes
305158,305161,1 | 305158 E17-KORNEGAY 115 305161 E17-TAPPFARM 115 1 | Lee - Wallace 115kV (OL056) | 121.01 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | Yes
304273,305158,1 | 304273 KORNEGAY SUB 115 305158 E17-KORNEGAY 115 1 | Lee - Wallace 115kV (OL056) | 120.77 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | Yes
304267,304500,1 | 304267 GRANTHAM 230 304500 WOMMACK230TT 230 1 | Lee - Wommack 230kV North (OL177) | 151.87 | 13 | 11 | 8 | 0 | 0 | 0 | 13 | 11 | 8 | 3 | 16 | Yes
304251,304267,1 | 304251 LEESUB230 TT 230 304267 GRANTHAM 230 1 | Lee - Wommack 230kV North (OL177) | 112.25 | 5 | 2 | 3 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 10 | Yes
304247,304251,1 | 304247 GA PAC TAP 230 304251 LEESUB230 TT 230 1 | Lee - Wommack 230kV South (OL136) | 130.02 | 8 | 7 | 6 | 0 | 0 | 0 | 8 | 7 | 6 | 3 | 15 | Yes
304247,305450,1 | 304247 GA PAC TAP 230 305450 SANDYBSOLTAP 230 1 | Lee - Wommack 230kV South (OL136) | 116.75 | 7 | 3 | 3 | 0 | 0 | 0 | 7 | 3 | 3 | 3 | 10 | Yes
304500,305450,1 | 304500 WOMMACK230TT 230 305450 SANDYBSOLTAP 230 1 | Lee - Wommack 230kV South (OL136) | 112.17 | 5 | 1 | 2 | 0 | 0 | 0 | 5 | 1 | 2 | 3 | 7 | Yes
304251,304261,2 | 304251 LEESUB230 TT 230 304261 LEESUB115STT 115 2 | Lee 230kV | 109.79 | 0 | 0 | 0 | 4 | 3 | 0 | 4 | 3 | 0 | 2 | 0 | Yes
304031,305154,1 | 304031 LEESEP115ETT 115 305154 E17-FREMONT 115 1 | Lee Plant - Black Creek SS 115kV West (OL053) | 100.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304238,305154,1 | 304238 BLACKCREEKTT 115 305154 E17-FREMONT 115 1 | Lee Plant - Black Creek SS 115kV West (OL053) | 97.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304030,305162,1 | 304030 LEESEP115WTT 115 305162 E17-ROSEWOOD 115 1 | Lee Plant - Selma 115kV (OL054) | 206.49 | 23 | 20 | 25 | 4 | 7 | 14 | 27 | 27 | 39 | 3 | 28 | Yes
304252,305162,1 | 304252 PRINCETON 115 305162 E17-ROSEWOOD 115 1 | Lee Plant - Selma 115kV (OL054) | 200.44 | 22 | 20 | 23 | 0 | 0 | 4 | 22 | 20 | 27 | 3 | 22 | Yes
304252,304302,1 | 304252 PRINCETON 115 304302 KENLY TAP 115 1 | Lee Plant - Selma 115kV (OL054) | 191.3 | 17 | 14 | 21 | 0 | 0 | 0 | 17 | 14 | 21 | 3 | 19 | Yes
304177,304302,1 | 304177 SELMA 115 TT 115 304302 KENLY TAP 115 1 | Lee Plant - Selma 115kV (OL054) | 180.95 | 14 | 12 | 20 | 0 | 0 | 0 | 14 | 12 | 20 | 3 | 17 | Yes
304248,306542,1 | 304248 ANSONVILLE 230 306542 6OAKBORO 230 1 | Lilesville - DPC Oakboro 230kV Black (OL085B) | 189.71 | 25 | 11 | 25 | 3 | 0 | 6 | 28 | 11 | 31 | 3 | 24 | Yes
304248,304358,1 | 304248 ANSONVILLE 230 304358 WADESBOW TAP 230 1 | Lilesville - DPC Oakboro 230kV Black (OL085B) | 179.9 | 17 | 12 | 25 | 1 | 0 | 3 | 18 | 12 | 28 | 3 | 22 | Yes
304358,304985,1 | 304358 WADESBOW TAP 230 304985 LILES SS TT 230 1 | Lilesville - DPC Oakboro 230kV Black (OL085B) | 179.9 | 17 | 12 | 25 | 1 | 0 | 3 | 18 | 12 | 28 | 3 | 22 | Yes
304985,305049,1 | 304985 LILES SS TT 230 305049 E11-BURNSVL 230 1 | Lilesville - DPC Oakboro 230kV White (OL085A) | 175.25 | 17 | 11 | 25 | 0 | 0 | 1 | 17 | 11 | 26 | 3 | 21 | Yes
305049,306542,1 | 305049 E11-BURNSVL 230 306542 6OAKBORO 230 1 | Lilesville - DPC Oakboro 230kV White (OL085A) | 172.41 | 17 | 11 | 25 | 0 | 0 | 0 | 17 | 11 | 25 | 3 | 21 | Yes
304350,304985,1 | 304350 PH SH BLACK 230 304985 LILES SS TT 230 1 | Lilesville - Rockingham 230kV Black (OL289B) | 105.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304349,304985,1 | 304349 PH SH WHITE 230 304985 LILES SS TT 230 1 | Lilesville - Rockingham 230kV White (OL289A) | 105.69 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304581,304597,1 | 304581 WHITEVL115TT 115 304597 WHITEVILTAP 115 1 | Marion - Whiteville 115kV (OL028) | 97.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304163,304174,1 | 304163 MILBUR115STT 115 304174 GARN PERSTOP 115 1 | Method - Milburnie 115kV South (OL062) | 115.49 | 6 | 7 | 10 | 0 | 0 | 0 | 6 | 7 | 10 | 3 | 6 | Yes
304152,304174,1 | 304152 GARNER 115 304174 GARN PERSTOP 115 1 | Method - Milburnie 115kV South (OL062) | 111.04 | 3 | 4 | 6 | 0 | 0 | 0 | 3 | 4 | 6 | 3 | 3 | Yes
304131,304162,1 | 304131 RAL WORTHDAL 230 304162 MILBUR230 TT 230 1 | Method - Milburnie 230kV (OL132) | 107.98 | 3 | 2 | 2 | 0 | 0 | 0 | 3 | 2 | 2 | 3 | 2 | Yes
304130,304131,1 | 304130 RAL EAST ST 230 304131 RAL WORTHDAL 230 1 | Method - Milburnie 230kV (OL132) | 101.06 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304156,304190,1 | 304156 ROL/SQD TAP 230 304190 WAKE 230 TT 230 1 | Milburnie - Wake 230kV (OL121) | 116.88 | 18 | 6 | 10 | 0 | 0 | 0 | 18 | 6 | 10 | 3 | 3 | Yes
304156,304276,1 | 304156 ROL/SQD TAP 230 304276 KNIGHT HODG 230 1 | Milburnie - Wake 230kV (OL121) | 105.61 | 3 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 2 | 0 | Yes
304162,304276,1 | 304162 MILBUR230 TT 230 304276 KNIGHT HODG 230 1 | Milburnie - Wake 230kV (OL121) | 103.36 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | Yes
304162,304090,1 | 304162 MILBUR230 TT 230 304090 MILBUR115NTT 115 1 | Milburnie 230kV | 102.54 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | Yes
304465,304506,1 | 304465 NEWBERN230TT 230 304506 DOVER 230 1 | New Bern - Wommack 230kV North (OL241) | 225.9 | 25 | 25 | 25 | 13 | 15 | 14 | 38 | 40 | 39 | 3 | 50 | Yes
304500,304506,1 | 304500 WOMMACK230TT 230 304506 DOVER 230 1 | New Bern - Wommack 230kV North (OL241) | 225.21 | 25 | 25 | 25 | 10 | 12 | 11 | 35 | 37 | 36 | 3 | 44 | Yes
304500,305524,1 | 304500 WOMMACK230TT 230 305524 Q424 230 1 | New Bern - Wommack 230kV South (OL268) | 161.25 | 25 | 25 | 25 | 7 | 8 | 7 | 32 | 33 | 32 | 3 | 38 | Yes
304465,305524,1 | 304465 NEWBERN230TT 230 305524 Q424 230 1 | New Bern - Wommack 230kV South (OL268) | 156.17 | 25 | 25 | 25 | 7 | 8 | 7 | 32 | 33 | 32 | 3 | 38 | Yes
304465,304466,1 | 304465 NEWBERN230TT 230 304466 NEWBER115NTT 115 1 | New Bern 230kV | 211.55 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | Yes
304465,304489,2 | 304465 NEWBERN230TT 230 304489 NEWBER115STT 115 2 | New Bern 230kV | 188.71 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | Yes
304466,304489,Z1 | 304466 NEWBER115NTT 115 304489 NEWBER115STT 115 Z1 | New Bern 230kV | 167.26 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | Yes
304723,900035,1 | 304723 CAMDENJCT TT 115 900035 ID_569014 115 1 | Robinson Plant - Camden Junction 115kV (OL076) | 118.57 | 0 | 1 | 14 | 0 | 0 | 0 | 0 | 1 | 14 | 2 | 8 | Yes
304721,900035,1 | 304721 BETHUNE TAP 115 900035 ID_569014 115 1 | Robinson Plant - Camden Junction 115kV (OL076) | 106.41 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
900009,900017,1 | 900009 ID_565080 230 900017 ID_566488 230 1 | Robinson Plant - Rockingham 230kV (OL155) | 104.91 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | Yes
304018,900009,1 | 304018 ROB2 230 TT 230 900009 ID_565080 230 1 | Robinson Plant - Rockingham 230kV (OL155) | 98.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304169,900049,1 | 304169 BUFFALO RD 230 900049 ID_569766 230 1 | Selma - Wake 230kV (OL225) | 116 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
304169,304199,1 | 304169 BUFFALO RD 230 304199 ARCH LODGE 230 1 | Selma - Wake 230kV (OL225) | 113.97 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
304188,304192,1 | 304188 PA-SELMA#3 230 304192 SELMA 230 TT 230 1 | Selma - Wake 230kV (OL225) | 113.09 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | Yes
304188,900049,1 | 304188 PA-SELMA#3 230 900049 ID_569766 230 1 | Selma - Wake 230kV (OL225) | 111.73 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304199,304274,1 | 304199 ARCH LODGE 230 304274 SHOTWELL SUB 230 1 | Selma - Wake 230kV (OL225) | 109.76 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304190,304274,1 | 304190 WAKE 230 TT 230 304274 SHOTWELL SUB 230 1 | Selma - Wake 230kV (OL225) | 108.25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | Yes
304039,304554,1 | 304039 SUTTON230 TT 230 304554 WILM N&O TAP 230 1 | Sutton Plant - Castle Hayne 230kV (OL118) | 113.63 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 0 | Yes
304552,304554,1 | 304552 WILM EAST 230 304554 WILM N&O TAP 230 1 | Sutton Plant - Castle Hayne 230kV (OL118) | 106.8 | 3 | 3 | 5 | 0 | 0 | 0 | 3 | 3 | 5 | 3 | 0 | Yes
304552,304577,1 | 304552 WILM EAST 230 304577 MURRAYVILLE 230 1 | Sutton Plant - Castle Hayne 230kV (OL118) | 99.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304550,304577,1 | 304550 CASTLEH230TT 230 304577 MURRAYVILLE 230 1 | Sutton Plant - Castle Hayne 230kV (OL118) | 95.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304582,304605,1 | 304582 DELCO230 TT 230 304605 RESILIENCE 230 1 | Sutton Plant - Delco 230kV (OL119) | 121.03 | 4 | 4 | 5 | 0 | 0 | 0 | 4 | 4 | 5 | 3 | 0 | Yes
304039,304605,1 | 304039 SUTTON230 TT 230 304605 RESILIENCE 230 1 | Sutton Plant - Delco 230kV (OL119) | 153.37 | 5 | 5 | 5 | 0 | 3 | 3 | 5 | 8 | 8 | 3 | 0 | Yes
304516,305995,1 | 304516 WILM BASF 230 305995 6SUTNORTH230 230 1 | Sutton Plant - Wallace 230kV (OL120) | 295.52 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304039,304520,1 | 304039 SUTTON230 TT 230 304520 WILM INVISTA 230 1 | Sutton Plant - Wallace 230kV (OL120) | 289.08 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304516,304578,1 | 304516 WILM BASF 230 304578 WILMCTFSHCR 230 1 | Sutton Plant - Wallace 230kV (OL120) | 249.07 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304534,304578,1 | 304534 WILM PRAX 230 304578 WILMCTFSHCR 230 1 | Sutton Plant - Wallace 230kV (OL120) | 247.76 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304520,304534,1 | 304520 WILM INVISTA 230 304534 WILM PRAX 230 1 | Sutton Plant - Wallace 230kV (OL120) | 246.31 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
305470,305880,1 | 305470 WILARDSOLTAP 230 305880 CROOKDSOLTAP 230 1 | Sutton Plant - Wallace 230kV (OL120) | 147.89 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 3 | 0 | Yes
304515,305880,1 | 304515 WALLACE230TT 230 305880 CROOKDSOLTAP 230 1 | Sutton Plant - Wallace 230kV (OL120) | 124.5 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
305470,305995,1 | 305470 WILARDSOLTAP 230 305995 6SUTNORTH230 230 1 | Sutton Plant - Wallace 230kV (OL120) | 103.77 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 0 | Yes
304035,304557,1 | 304035 SUTTON115 TT 115 304557 WILM GNF 115 1 | Sutton Plant - Wilmington GNF 115kV (OL101) | 108.41 | 20 | 15 | 16 | 0 | 0 | 0 | 20 | 15 | 16 | 3 | 17 | Yes
304004,304342,1 | 304004 TILLERY115TT 115 304342 BADIN #1 115 1 | Tillery Plant - Alcoa Badin 115kV Black (OL102B) | 176.87 | 16 | 6 | 24 | 10 | 0 | 6 | 26 | 6 | 30 | 3 | 20 | Yes
304004,304343,1 | 304004 TILLERY115TT 115 304343 BADIN #2 115 1 | Tillery Plant - Alcoa Badin 115kV White (OL102A) | 172.59 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | Yes
304515,304517,1 | 304515 WALLACE230TT 230 304517 WALLACE115TT 115 1 | Wallace 230kV | 154.92 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | Yes
304734,306416,1 | 304734 WATEREE115TT 115 306416 WATEREE 100 1 | Wateree Plant | 140.42 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | Yes
304734,306416,2 | 304734 WATEREE115TT 115 306416 WATEREE 100 2 | Wateree Plant | 140.42 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | Yes
304046,304047,1 | 304046 WSPOON230 TT 230 304047 WSPOON115 TT 115 1 | Weatherspoon Plant | 131.99 | 0 | 0 | 0 | 13 | 15 | 13 | 13 | 15 | 13 | 3 | 18 | Yes
304047,304574,1 | 304047 WSPOON115 TT 115 304574 BLADENBORO 115 1 | Weatherspoon Plant - Delco 115kV (OL104) | 155.33 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304576,304583,1 | 304576 KINGS BLUFF 115 304583 DELCO115E TT 115 1 | Weatherspoon Plant - Delco 115kV (OL104) | 148.61 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304570,304576,1 | 304570 CLARKTON 115 304576 KINGS BLUFF 115 1 | Weatherspoon Plant - Delco 115kV (OL104) | 147.06 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304570,304571,1 | 304570 CLARKTON 115 304571 ELIZTOWN TAP 115 1 | Weatherspoon Plant - Delco 115kV (OL104) | 146.72 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
304571,304574,1 | 304571 ELIZTOWN TAP 115 304574 BLADENBORO 115 1 | Weatherspoon Plant - Delco 115kV (OL104) | 138.48 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | Yes
305138,305380,1 | 305138 E15-LBRTYPT 230 305380 COLINSOL-TAP 230 1 | Weatherspoon Plant - Fayetteville 230kV (OL122) | 97.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304047,305099,1 | 304047 WSPOON115 TT 115 305099 E10-WESTLUMB 115 1 | Weatherspoon Plant - Libbey Owens Ford 115kV (OL049) | 98.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304047,304432,1 | 304047 WSPOON115 TT 115 304432 PA-LUMB#2 115 1 | Weatherspoon Plant - Raeford 115kV (OL108) | 98.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
304363,305106,1 | 304363 WESTENW115TT 115 305106 E14-EASTWOOD 115 1 | West End - Southern Pines 115kV (OL153) | 131.71 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 31 | 0 | 1 | 12 | Yes
304592,305106,1 | 304592 HILCRS115TT 115 305106 E14-EASTWOOD 115 1 | West End - Southern Pines 115kV (OL153) | 115.75 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 12 | 0 | 1 | 0 | Yes
304361,304362,1 | 304361 WESTEND230TT 230 304362 WESTENE115TT 115 1 | West End 230kV | 138.13 | 0 | 5 | 0 | 0 | 16 | 7 | 0 | 21 | 7 | 2 | 7 | Yes
304361,304363,2 | 304361 WESTEND230TT 230 304363 WESTENW115TT 115 2 | West End 230kV | 137.69 | 0 | 5 | 0 | 0 | 16 | 7 | 0 | 21 | 7 | 2 | 7 | Yes
304362,304363,Z1 | 304362 WESTENE115TT 115 304363 WESTENW115TT 115 Z1 | West End 230kV | 96.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Below 100%
304500,304510,2 | 304500 WOMMACK230TT 230 304510 WOMACKW115TT 115 2 | Wommack 230kV | 127.67 | 0 | 1 | 0 | 9 | 8 | 7 | 9 | 9 | 7 | 3 | 19 | Yes
304500,304507,1 | 304500 WOMMACK230TT 230 304507 WOMACKE115TT 115 1 | Wommack 230kV | 103.53 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | Yes