## MVST_Alternative_Solutions
MVST Solutions - Notes on Alternatives
Cluster Name | Alternative Solution | Solution Notes | Preliminary Solution
Wateree Cluster | Advanced Conductors | Leverage existing ROW, lower risk, mostly rural, significant time to construct and many outages to complete all upgrades along the path. (Operations / Timeline risk) -$300M+
Wateree Cluster | Open Wateree B&W 100kV Line | Do not want to leave open all the time due to limited grid sources on both sides of the line. Increased reliability risk. Need to open Wateree lines likely to increase over time. (Operations Risk)
Wateree Cluster | Switchable Series Reactor | Adding additional impedance will defer the need for upgrades and buy time for a longer term solution but overloads still likely. (Effectiveness) | X
Wateree Cluster | Rebuild Winnsboro BL/WH 100kV Line | Leverage existing ROW but complete re-build of decommissioned line. | X
Wateree Cluster | New Bush River to Darlington 230kV line | Potential to route along existing 100 kV ROW, requires expanding ROW. 108-110 miles. Adds flow to lines by exporting DEC excess solar toward Darlington. (Effectiveness)
Wateree Cluster | New Pacolet to Darlington 230kV line | Potential to route along existing 100 kV ROW, requires expanding ROW. 108-110 miles. Adds flow to lines by exporting DEC excess solar toward Darlington. (Effectiveness)
Badin Cluster | Advanced Conductors for Tillery-Badin | Badin solutions are right-sized for expected long-term need instead of next cluster. Requires coordination with Yadkin / Affected System. | X
Badin Cluster | Open Tillery-Badin 115kV line | Potential as a short-term switching solution but potential reliability impacts to Yadkin's system
Badin Cluster | Series Reactor on Blewett-Tillery 115kV line | Reactor appears sufficient to address MVST Needs on Blewett Tillery but does not resolve loading at Badin.
DEC 500 kV to 230 kV | New 500/230 kV Cliffside Bank | New bank requires additional underbuild upgrades to avoid new overloads. | X
DEC 500 kV to 230 kV | Advanced Power Flow Control Device | Additional impedance only addresses minor overloads and does not add additional capacity to system. (Effectiveness)
DEC 500 kV to 230 kV | Switchable Series Reactors | Additional impedance only addresses minor overloads and does not add additional capacity to system. (Effectiveness)
Harley Hogback | Battery at Hendersonville Tie or Campobello Tie | Battery may be helpful in one case but increased overloads in another. Already many batteries in model with higher overloads. (Effectiveness)
Harley Hogback | New Tiger to Asheville 230kV line | Potential long-term benefit for tie line capacity between DEC and CPLW. Harley Hogback issues are local overloads. No guarantee of ROW expansion. ~50 miles through rough terrain.
Harley Hogback | Raise Voltage on 44kV lines to 100kV | Many 44kV circuits have enough ROW to support 100kV lines. Substation work required to add new 100 kV circuit. Identified 44kV circuits already rebuilt or planned for 100 kV towers. | X
Woodruff Tie 100kV | Re-build Woodruff Tie 100kV and upgrade 44kV lines to 100kV | Leverage existing ROW in growing rural area. Some ROW encroachment challenges. Significant expansion of Woodruff substation required. | X
Woodruff Tie 100kV | New Hodges to Pacolet 230kV | Around 50 miles of new ROW, some in developed areas around Greenville Spartanburg. (Constructability Risk)
Woodruff Tie 100kV | New Hodges to Tiger 230kV | Around 50 miles of new ROW, some in developed areas around Greenville Spartanburg. (Constructability Risk)
Woodruff Tie 100kV | New Laurens - Woodruff 100 kV | Screened but limited effectiveness for addressing MVST Needs by itself
Woodruff Tie 100kV | Woodruff - Sock Hill Ret Tap - 44 to 100 kV Conversion | Screened but limited effectiveness for addressing MVST Needs by itself
None | New Belton to Hodges BL/WH 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Belton to Lee CC BL/WH 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Buzzard Roost to Clinton 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Cliffside - Newport 500 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Coronaca - Laurens BL 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Goose Creek WH 230 kV line (Oakboro - Morning Star) | Screened but limited effectiveness for addressing MVST Needs
None | New Greenwood - Hodges BL/WH 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Laurens - Hodges 100 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Parkwood - Durham 500 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Pleasant Garden - Person 500 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Pleasant Garden - Richmond 500 kV | Screened but limited effectiveness for addressing MVST Needs
None | New Sandy Ridge Wh 230 kV (Newport - Morning Star) | Screened but limited effectiveness for addressing MVST Needs
None | New Cliffside - Tiger 230 kV | Screened but limited effectiveness for addressing MVST Needs
None | Extend Robat BL/WH 100 kV to Leeds | Screened but limited effectiveness for addressing MVST Needs

## Needs by Cluster ->
Notes:
Each tab includes MVST Needs that were evaluated as part of that Solutions cluster
The most limiting contingencies were added
The rest of the information was sourced directly from the Needs shared in March 2025

## Wateree
Wateree Tie Cluster
Duke Energy Progress Overloads
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Monitored Branch | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_CSM_br1dn | ctpc34s_r3_MVST_Scenario1_CSM_br2dn | ctpc34s_r3_MVST_Scenario1_CSM_hardn | ctpc34s_r3_MVST_Scenario1_CSM_rob2dn | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_SP_br1dn | ctpc34s_r3_MVST_Scenario1_SP_br2dn | ctpc34s_r3_MVST_Scenario1_SP_hardn | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_S90_br1dn | ctpc34s_r3_MVST_Scenario1_S90_br2dn | ctpc34s_r3_MVST_Scenario1_S90_hardn | ctpc34s_r3_MVST_Scenario1_S90_rob2dn | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S110_br1dn | ctpc34s_r3_MVST_Scenario1_S110_br2dn | ctpc34s_r3_MVST_Scenario1_S110_hardn | ctpc34s_r3_MVST_Scenario1_S110_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario1_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario1_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_CSM_br1dn | ctpc34s_r3_MVST_Scenario2_CSM_br2dn | ctpc34s_r3_MVST_Scenario2_CSM_hardn | ctpc34s_r3_MVST_Scenario2_CSM_rob2dn | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_SP_br1dn | ctpc34s_r3_MVST_Scenario2_SP_br2dn | ctpc34s_r3_MVST_Scenario2_SP_hardn | ctpc34s_r3_MVST_Scenario2_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_S90_br1dn | ctpc34s_r3_MVST_Scenario2_S90_br2dn | ctpc34s_r3_MVST_Scenario2_S90_hardn | ctpc34s_r3_MVST_Scenario2_S90_rob2dn | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S110_br1dn | ctpc34s_r3_MVST_Scenario2_S110_br2dn | ctpc34s_r3_MVST_Scenario2_S110_hardn | ctpc34s_r3_MVST_Scenario2_S110_rob2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario2_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario2_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_CSM_br1dn | ctpc34s_r3_MVST_Scenario3_CSM_br2dn | ctpc34s_r3_MVST_Scenario3_CSM_hardn | ctpc34s_r3_MVST_Scenario3_CSM_rob2dn | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_SP_br1dn | ctpc34s_r3_MVST_Scenario3_SP_br2dn | ctpc34s_r3_MVST_Scenario3_SP_hardn | ctpc34s_r3_MVST_Scenario3_SP_rob2dn | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_S90_br1dn | ctpc34s_r3_MVST_Scenario3_S90_br2dn | ctpc34s_r3_MVST_Scenario3_S90_hardn | ctpc34s_r3_MVST_Scenario3_S90_rob2dn | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S110_br1dn | ctpc34s_r3_MVST_Scenario3_S110_br2dn | ctpc34s_r3_MVST_Scenario3_S110_hardn | ctpc34s_r3_MVST_Scenario3_S110_rob2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34s_r3_MVST_Scenario3_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario3_SP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_br1dn | ctpc34w_r3_MVST_Scenario1_WP_br2dn | ctpc34w_r3_MVST_Scenario1_WP_hardn | ctpc34w_r3_MVST_Scenario1_WP_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_waltdn | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W90_br1dn | ctpc34w_r3_MVST_Scenario1_W90_br2dn | ctpc34w_r3_MVST_Scenario1_W90_hardn | ctpc34w_r3_MVST_Scenario1_W90_rob2dn | ctpc34w_r3_MVST_Scenario1_W90_waltdn | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W110_br1dn | ctpc34w_r3_MVST_Scenario1_W110_br2dn | ctpc34w_r3_MVST_Scenario1_W110_hardn | ctpc34w_r3_MVST_Scenario1_W110_rob2dn | ctpc34w_r3_MVST_Scenario1_W110_waltdn | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario1_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario1_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_br1dn | ctpc34w_r3_MVST_Scenario2_WP_br2dn | ctpc34w_r3_MVST_Scenario2_WP_hardn | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W90_br1dn | ctpc34w_r3_MVST_Scenario2_W90_br2dn | ctpc34w_r3_MVST_Scenario2_W90_hardn | ctpc34w_r3_MVST_Scenario2_W90_rob2dn | ctpc34w_r3_MVST_Scenario2_W90_waltdn | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W110_br1dn | ctpc34w_r3_MVST_Scenario2_W110_br2dn | ctpc34w_r3_MVST_Scenario2_W110_hardn | ctpc34w_r3_MVST_Scenario2_W110_rob2dn | ctpc34w_r3_MVST_Scenario2_W110_waltdn | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario2_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_waltdn | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_br1dn | ctpc34w_r3_MVST_Scenario3_WP_br2dn | ctpc34w_r3_MVST_Scenario3_WP_hardn | ctpc34w_r3_MVST_Scenario3_WP_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_waltdn | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W90_br1dn | ctpc34w_r3_MVST_Scenario3_W90_br2dn | ctpc34w_r3_MVST_Scenario3_W90_hardn | ctpc34w_r3_MVST_Scenario3_W90_rob2dn | ctpc34w_r3_MVST_Scenario3_W90_waltdn | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W110_br1dn | ctpc34w_r3_MVST_Scenario3_W110_br2dn | ctpc34w_r3_MVST_Scenario3_W110_hardn | ctpc34w_r3_MVST_Scenario3_W110_rob2dn | ctpc34w_r3_MVST_Scenario3_W110_waltdn | ctpc34w_r3_MVST_Scenario3_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario3_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_waltdn | Total | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
304730,304725,1 | 304730 | CAMDEN230 TT | 304725 | CAMDEN115 TT | 1 | 230 | 304730 CAMDEN230 TT 230 304725 CAMDEN115 TT 115 1 | Substation | Camden 230kV | 230/115 kV Transformer | ROBINSON-PLANT-CAMDEN-JUNCTION-115KV-LINE | [19 empty] | 92.81 |  |  | 92.16 |  |  | 90.1 |  |  |  |  | 106.76 | 103.57 | 103.44 | 106.47 | 95.33 | 95.75 | 92.4 | 92.25 | 95.18 | [6 empty] | 114.39 | 111.49 | 111.34 | 114.28 | 103.13 | 98.91 | 96.47 | 96.35 | 99.23 |  | 115.42 | 113.22 | 113.09 | 115.83 | 105.5 | 108.13 | 105.77 | 105.64 | 108.4 | 97.8 | 104.73 | 102.84 | 102.72 | 105.47 | 95.1 | 123.8 | 121.94 | 121.8 | 124.46 | 114.07 | [77 empty] | 93.88 | 93.16 | 91.69 | 91.55 | 94.54 |  | 93.07 | 115.83 | 124.46 | 0 | 9 | 18 | 0 | 0 | 0 | 0 | 9 | 18 | 2 | 9 | NO |  |  |  |  | Yes | 0 | No
304723,304726,1 | 304723 | CAMDENJCT TT | 304726 | CAMDEN DUSTY | 1 | 115 | 304723 CAMDENJCT TT 115 304726 CAMDEN DUSTY 115 1 | Line | Camden - Camden Junction 115kV | 115 kV Line | CAMDEN-JUNCTION-DPC-WATEREE-PLANT-115KV-LINE | 105.64 | 90.59 | 90.59 | 93.07 | [10 empty] | 92.79 |  |  |  |  | 100.86 | [5 empty] | 96.04 | [5 empty] | 91.95 | 91.7 | 94.33 | 91.29 | [11 empty] | 93.22 | 93.02 | 95.74 | 92.62 | 115.65 | 102.75 | 102.78 | 105.03 |  |  |  |  | 91.02 | [11 empty] | 90.99 | 91.64 | 91.44 | 93.95 | 91.39 | [84 empty] | 94.33 | 115.65 | 2 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 4 | 2 | 5 | NO |  |  | 179.83 | 284.45 | Yes | 2 | No
304726,304738,1 | 304726 | CAMDEN DUSTY | 304738 | CAMD KENDAL | 1 | 115 | 304726 CAMDEN DUSTY 115 304738 CAMD KENDAL 115 1 | Line | Camden - Camden Junction 115kV | 115 kV Line | CAMDEN-CAMDEN-DUPONT-115KV-LINE | 92.58 | [29 empty] | 99.4 | 103.38 | 103.14 | 105.93 | 102.33 |  |  |  | 91.5 | [6 empty] | 101.17 | 105.07 | 104.85 | 107.72 | 104 | 102.62 |  |  | 92.14 |  | 95.97 | 101.13 | 100.92 | 103.45 | 100.8 |  | 92.02 | 91.81 | 94.36 | 91.31 |  |  |  | 90.6 |  | 99.93 | 104.68 | 104.47 | 107.17 | 103.91 | [84 empty] | 105.93 | 107.72 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 9 | 9 | 2 | 9 | NO |  |  | 168.45 | 184.9 | Yes | 2 | No
304716,304725,1 | 304716 | CAMDEN TAP | 304725 | CAMDEN115 TT | 1 | 115 | 304716 CAMDEN TAP 115 304725 CAMDEN115 TT 115 1 | Line | Camden - Camden Junction 115kV | 115 kV Line | CAMDEN-CAMDEN-DUPONT-115KV-LINE | [15 empty] | 90.1 |  | 92.98 |  |  |  |  | 90.95 | [7 empty] | 124.19 | 127.84 | 127.59 | 130.58 | 126.23 | 106.41 | 110.09 | 109.87 | 112.7 | 108.43 | 107 | 110.6 | 110.39 | 113.3 | 109.08 | 126.57 | 130.09 | 129.86 | 132.92 | 128.38 | [5 empty] | 122.43 | 126.77 | 126.55 | 129.33 | 125.72 | 109.44 | 113.75 | 113.53 | 116.27 | 112.47 | 109.55 | 114.22 | 114.01 | 116.8 | 113.26 | 127.36 | 131.29 | 131.08 | 134.02 | 129.8 | [81 empty] | 90.99 |  |  | 130.58 | 134.02 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | 2 | 10 | NO |  |  | 149.01 |  | Yes | 1 | No
304716,304724,1 | 304716 | CAMDEN TAP | 304724 | CAMD DEKALB | 1 | 115 | 304716 CAMDEN TAP 115 304724 CAMD DEKALB 115 1 | Line | Camden - Camden Junction 115kV | 115 kV Line | CAMDEN-CAMDEN-DUPONT-115KV-LINE | [30 empty] | 115.05 | 118.79 | 118.55 | 121.49 | 117.33 | 98.56 | 102.3 | 102.08 | 104.88 | 100.76 | 97.65 | 101.29 | 101.08 | 103.94 | 99.93 | 117.27 | 120.9 | 120.68 | 123.68 | 119.35 | [5 empty] | 112.84 | 117.41 | 117.19 | 119.92 | 116.55 | 101.38 | 105.8 | 105.58 | 108.27 | 104.66 | 99.47 | 104.35 | 104.14 | 106.86 | 103.59 | 117.57 | 121.73 | 121.52 | 124.4 | 120.43 | [84 empty] | 121.49 | 124.4 | 0 | 17 | 19 | 0 | 0 | 0 | 0 | 17 | 19 | 2 | 10 | NO |  |  | 155.4 |  | Yes | 1 | No
304724,304738,1 | 304724 | CAMD DEKALB | 304738 | CAMD KENDAL | 1 | 115 | 304724 CAMD DEKALB 115 304738 CAMD KENDAL 115 1 | Line | Camden - Camden Junction 115kV | 115 kV Line | CAMDEN-CAMDEN-DUPONT-115KV-LINE | [30 empty] | 102.01 | 105.93 | 105.69 | 108.53 | 104.76 |  | 91.38 | 91.16 | 93.87 | 90.08 |  |  |  | 91.22 |  | 103.92 | 107.75 | 107.53 | 110.44 | 106.54 | 99.67 |  |  |  |  | 98.94 | 103.93 | 103.72 | 106.32 | 103.45 |  | 94.52 | 94.3 | 96.91 | 93.67 |  | 90.6 | 90.4 | 92.95 | 90.28 | 103.17 | 107.75 | 107.54 | 110.29 | 106.82 | [84 empty] | 108.53 | 110.44 | 0 | 10 | 9 | 0 | 0 | 0 | 0 | 10 | 9 | 2 | 9 | NO |  |  | 165.39 |  | Yes | 1 | No
304731,304732,1 | 304731 | CAMD DUP TT | 304732 | ELGIN TAP | 1 | 115 | 304731 CAMD DUP TT 115 304732 ELGIN TAP 115 1 | Line | Camden DuPont - DPC Wateree Plant 115kV | 115 kV Line | CAMDEN-JUNCTION-DPC-WATEREE-PLANT-115KV-LINE | 124.42 | 113.24 | 112.96 | 119.92 | 92.42 | 149.11 | 137.53 | 137.22 | 144.57 | 145.07 | 132.87 | 132.55 | 139.96 | 110.4 | 176.41 | 164.33 | 164.03 | 171.57 | 141.65 | 190.39 | 178.46 | 178.13 | 185.6 | 155.43 | 115.08 | 175.71 | 165.02 | 164.73 | 171.8 | 143.99 | 192.27 | 182.38 | 182.05 | 189 | 164.24 | 171.26 | 160.77 | 160.46 | 167.41 | 141.7 | 157.95 | 150.19 | 149.93 | 156.26 | 132.86 | 212.66 | 202.8 | 202.45 | 209.72 | 181.38 | 198.64 | 190.03 | 189.73 | 196.39 | 169.44 | 218.98 | 209.97 | 209.69 | 216.51 | 189.06 | 204.56 | 195.21 | 194.92 | 201.59 | 174.14 | 186.77 | 179.05 | 178.79 | 185.4 | 159.5 | 235.87 | 226.54 | 226.21 | 233.35 | 204.92 | 91.21 | [20 empty] | 112.03 | 110.6 | 104.29 | 104.03 | 109.81 |  | 110.4 | [19 empty] | 107.57 | 106.19 | 102.07 | 101.81 | 107.14 |  | 106.02 |  |  | 125.94 | 124.65 | 119.57 | 119.33 | 124.92 | 103.79 | 124.49 | 119.82 | 118.49 | 111.56 | 111.33 | 116.88 | 95.11 | 118.39 | 99.74 | 98.48 | 93.02 | 92.84 | 98.4 |  | 98.27 | 139.63 | 138.37 | 133.57 | 133.33 | 138.81 | 115.75 | 138.22 | 218.98 | 235.87 | 24 | 25 | 25 | 6 | 6 | 20 | 30 | 31 | 45 | 3 | 35 | NO |  |  | 230.11 | 810.89 | Yes | 2 | No
304732,304734,1 | 304732 | ELGIN TAP | 304734 | WATEREE115TT | 1 | 115 | 304732 ELGIN TAP 115 304734 WATEREE115TT 115 1 | Line | Camden DuPont - DPC Wateree Plant 115kV | 115 kV Line | CAMDEN-JUNCTION-DPC-WATEREE-PLANT-115KV-LINE | 93.08 |  |  |  |  | 111.4 | 102.29 | 102.04 | 107.81 | 108.91 | 99.32 | 99.07 | 104.89 |  | 132.14 | 122.64 | 122.41 | 128.33 | 104.82 | 143.85 | 134.46 | 134.2 | 140.08 | 116.35 |  | 132.97 | 124.61 | 124.39 | 129.91 | 108.19 | 145.14 | 137.38 | 137.12 | 142.59 | 123.12 | 129.42 | 121.18 | 120.94 | 126.4 | 106.17 | 117.95 | 111.85 | 111.66 | 116.6 | 98.36 | 161.17 | 153.45 | 153.17 | 158.89 | 136.6 | 150.87 | 144.2 | 143.94 | 149.15 | 128.08 | 165.95 | 158.93 | 158.71 | 164.09 | 142.49 | 155.54 | 148.23 | 148 | 153.24 | 131.67 | 140.07 | 134.15 | 133.95 | 139.12 | 118.86 | 179.28 | 171.74 | 171.49 | 177.36 | 154.78 | [21 empty] | 93.36 | 92.11 |  |  | 91.41 |  | 91.93 | [28 empty] | 105.43 | 104.31 | 99.87 | 99.67 | 104.56 |  | 104.16 | 100.73 | 99.58 | 93.42 | 93.22 | 98.09 |  | 99.49 | [7 empty] | 117.43 | 116.34 | 112.15 | 111.94 | 116.74 | 96.52 | 116.2 | 165.95 | 179.28 | 16 | 24 | 25 | 0 | 0 | 6 | 16 | 24 | 31 | 3 | 28 | NO |  |  | 175.45 | 781.04 | Yes | 2 | No
304723,900035,1 | 304723 | CAMDENJCT TT | 900035 | ID_569014 | 1 | 115 | 304723 CAMDENJCT TT 115 900035 ID_569014 115 1 | Line | Robinson Plant - Camden Junction 115kV | 115 kV Line | CAMDEN-SCPSA-LUGOFF-230KV-LINE | [25 empty] | 98.02 | 90.06 |  | 93.03 |  | 93.49 | [14 empty] | 103.99 | 96.96 | 96.85 | 99.76 |  | 112.3 | 104.77 | 104.7 | 107.64 | 92.84 | 110.87 | 103.88 | 103.81 | 106.57 | 91.6 | 103.38 | 96.18 | 96.1 | 98.88 |  | 100.1 | 93.4 | 93.33 | 96.07 |  | 118.57 | 111.6 | 111.5 | 114.39 | 99.89 | [84 empty] | 110.87 | 118.57 | 0 | 1 | 14 | 0 | 0 | 0 | 0 | 1 | 14 | 2 | 8 | NO |  |  | 104.61 |  | Yes | 1 | No
304721,900035,1 | 304721 | BETHUNE TAP | 900035 | ID_569014 | 1 | 115 | 304721 BETHUNE TAP 115 900035 ID_569014 115 1 | Line | Robinson Plant - Camden Junction 115kV | 115 kV Line | CAMDEN-SCPSA-LUGOFF-230KV-LINE | [45 empty] | 91.48 | [9 empty] | 98.49 | 91.99 | 91.92 | 94.65 |  | 90.98 | [9 empty] | 106.41 | 99.65 | 99.55 | 102.41 | [85 empty] | 98.49 | 106.41 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | NO |  |  |  | 536.44 | Yes | 1 | No
304734,306416,1 | 304734 | WATEREE115TT | 306416 | WATEREE | 1 | 115 | 304734 WATEREE115TT 115 306416 WATEREE 100 1 | Substation | Wateree Plant | 115/100 kV Transformer | WATEREE115TT-WATEREE-115-100-#2 | [5 empty] | 91.13 | [8 empty] | 107.33 | 98.89 | 98.72 | 103.49 |  | 117.32 | 109.07 | 108.87 | 113.58 | 93.72 |  | 109.51 | 102.47 | 102.3 | 106.65 |  | 113.89 | 107.06 | 106.89 | 111.3 | 92.89 | 102.55 | 95.31 | 95.13 | 99.49 |  | 93.74 |  |  | 91.41 |  | 126.74 | 120.42 | 120.22 | 124.56 | 106.11 | 123.97 | 118.52 | 118.37 | 122.41 | 105.29 | 129.83 | 124.59 | 124.43 | 128.46 | 111.26 | 123.98 | 117.98 | 117.81 | 121.9 | 104.19 | 111.28 | 106.57 | 106.42 | 110.44 | 93.42 | 140.42 | 135.52 | 135.34 | 139.3 | 121.84 | [56 empty] | 95.15 | 94.24 |  |  | 93.85 |  | 94.12 | 91.61 | 90.62 |  |  |  |  | 90.54 | [7 empty] | 106.18 | 105.3 | 101.03 | 100.85 | 105.12 |  | 105.18 | 129.83 | 140.42 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | NO |  |  | 146.61 | 1294.29 | Yes | 3 | No
304734,306416,2 | 304734 | WATEREE115TT | 306416 | WATEREE | 2 | 115 | 304734 WATEREE115TT 115 306416 WATEREE 100 2 | Substation | Wateree Plant | 115/100 kV Transformer | WATEREE115TT-WATEREE-115-100-#1 | [5 empty] | 91.13 | [8 empty] | 107.33 | 98.89 | 98.72 | 103.49 |  | 117.32 | 109.07 | 108.87 | 113.58 | 93.72 |  | 109.51 | 102.47 | 102.3 | 106.65 |  | 113.89 | 107.06 | 106.89 | 111.3 | 92.89 | 102.55 | 95.31 | 95.13 | 99.49 |  | 93.74 |  |  | 91.41 |  | 126.74 | 120.42 | 120.22 | 124.56 | 106.11 | 123.97 | 118.52 | 118.37 | 122.41 | 105.29 | 129.83 | 124.59 | 124.43 | 128.46 | 111.26 | 123.98 | 117.98 | 117.81 | 121.9 | 104.19 | 111.28 | 106.57 | 106.42 | 110.44 | 93.42 | 140.42 | 135.52 | 135.34 | 139.3 | 121.84 | [56 empty] | 95.15 | 94.24 |  |  | 93.85 |  | 94.12 | 91.61 | 90.62 |  |  |  |  | 90.54 | [7 empty] | 106.18 | 105.3 | 101.03 | 100.85 | 105.12 |  | 105.18 | 129.83 | 140.42 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | NO |  |  | 146.61 | 1294.29 | Yes | 3 | No
Duke Energy Carolinas Overloads
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage |  | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
306346,306376,1 | 306346 | BOWATER | 306376 | GUARDIAN | 1 | 100 |  | Line | EDGEMOOR B&W NORTH | 100 kV Line | P2 - MONROE_BJB | 127.7 | 125.8 | 142.6 | 128.4 | 131.5 | 134.7 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 142.6 | 2 | 3 | NO |  |  |  | 2227.2 | Yes | 3 | No
306369,306376,Z1 | 306369 | GITI TAP | 306376 | GUARDIAN | 1 | 100 |  | Line | EDGEMOOR B&W NORTH | 100 kV Line | P2 - MONROE_BJB | 112.4 | 111.1 | 125.9 | 113.1 | 116 | 118.5 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 125.9 | 2 | 3 | NO |  |  |  | 2082.2 | Yes | 3 | No
308689,308747,1 | 308689 | EDGMR STR126 | 308747 | IBHS | 1 | 100 |  | Line | EDGEMOOR B&W SOUTH | 100 kV Line | P2 - MONROE_BJB | 123.6 | 115.4 | 132.8 | 117.4 | 121.1 | 131.5 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 132.8 | 2 | 3 | NO |  |  |  | 2099.2 | Yes | 3 | No
306369,308689,1 | 306369 | GITI TAP | 308689 | EDGMR STR126 | 1 | 100 |  | Line | EDGEMOOR B&W SOUTH | 100 kV Line | P2 - MONROE_BJB | 123.5 | 115.3 | 132.8 | 117.3 | 121.1 | 131.4 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 132.8 | 2 | 3 | NO |  |  |  | 2099.2 | Yes | 3 | No
306375,308747,1 | 306375 | GT FALL1 | 308747 | IBHS | 1 | 100 |  | Line | EDGEMOOR B&W SOUTH | 100 kV Line | P2 - MONROE_BJB | 105.7 | 0 | 96.2 | 0 | 0 | 116.1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 116.1 | 2 | 2 | NO |  |  | 101 | 1002.6 | Yes | 3 | No
306327,306346,1 | 306327 | ROCKH6 | 306346 | BOWATER | 1 | 100 |  | Line | HUCKLEBERRY BL | 100 kV Line | P2 - MONROE_BJB | 97.3 | 101 | 121 | 98.6 | 105 | 114.5 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 121 | 2 | 2 | YES |  |  |  | 1972.2 | Yes | 3 | No
306327,306399,1 | 306327 | ROCKH6 | 306399 | ROCK H12T | 1 | 100 |  | Line | HUCKLEBERRY BL | 100 kV Line | P2 - MONROE_BJB | [5 empty] | 96.2 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 96.2 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306375,306408,1 | 306375 | GT FALL1 | 306408 | SPRS TAP | 1 | 100 |  | Line | LANDSFORD BL | 100 kV Line | P2 - BOWATER_YB | 107.2 | 0 | 105.3 | 0 | 96.8 | 148.9 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 148.9 | 2 | 2 | NO |  |  |  | 1768.2 | Yes | 2 | No
306346,306408,1 | 306346 | BOWATER | 306408 | SPRS TAP | 1 | 100 |  | Line | LANDSFORD BL | 100 kV Line | P2 - BOWATER_YB | 109.2 | 104.6 | 118.9 | 106.8 | 110.5 | 143.1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 143.1 | 2 | 3 | NO |  |  |  | 1111.5 | Yes | 2 | No
306346,309708,1 | 306346 | BOWATER | 309708 | RUTAB PV | 1 | 100 |  | Line | LANDSFORD WH | 100 kV Line | P2 - MONROE_BJB | 119.2 | 109.5 | 124.2 | 110.9 | 114.2 | 126.6 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 126.6 | 2 | 3 | NO |  |  |  | 2227.2 | Yes | 3 | No
306375,309708,1 | 306375 | GT FALL1 | 309708 | RUTAB PV | 1 | 100 |  | Line | LANDSFORD WH | 100 kV Line | P3 - RBPVGM - LANDSFORDB_N | 113.3 | 105.6 | 108.4 | 108.4 | 112.5 | 113.3 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 113.3 | 2 | 3 | NO |  |  |  | 961.1 | No | 1 | No
306375,309837,2 | 306375 | GT FALL1 | 309837 | RANGERLN | 2 | 100 |  | Line | WATEREE B&W | 100 kV Line | P3 - CAT1GM -PARRB | 269.3 | 235 | 253.1 | 229.7 | 260.1 | 269.3 | 221.3 | 229.6 | 201.8 | 254.3 | 277 | 248.3 | 257.2 | 238.4 | 270.2 | 146.7 | 155.2 | 135.1 | 176.4 | 128.2 | 143.5 | 121.9 | 155 | 183 | 202.1 | 176.5 | 209.9 | 277 | 3 | 9 | YES | 115.5 |  | 265.7 | 1826.9 | Yes | 5 | No
306416,309837,2 | 306416 | WATEREE | 309837 | RANGERLN | 2 | 100 |  | Line | WATEREE B&W | 100 kV Line | P3 - CAT1GM -NEWPORT_XFMR | 206.6 | 190.4 | 210.5 | 183.3 | 220.3 | 206.6 | 220.7 | 228.6 | 201.3 | 253.4 | 276.4 | 247.5 | 256.2 | 237.9 | 269.5 | 146.2 | 154.7 | 134.7 | 176 | 127.8 | 142.9 | 121.6 | 154.6 | 182.5 | 201.4 | 176.1 | 209.3 | 276.4 | 3 | 9 | YES | 115 |  | 266 | 1606.9 | Yes | 5 | No
304734,306416,1 | 304734 | WATEREE115TT | 306416 | WATEREE | 1 | 115 |  | Substation | WATEREE PLANT #1 | 115/100 kV Transformer | P3 - CAT1GM - WATERE1001152 | 0 | 101 | 127.3 | 97.1 | 120.2 | 0 | 116.2 | 97.8 | 111.8 | 135.3 | 128.4 | 134.1 | 113.7 | 130.7 | 148.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 98.1 | 114.3 | 148.2 | 3 | 4 | NO |  |  |  | 127.5 | Yes | 1 | No
304734,306416,2 | 304734 | WATEREE115TT | 306416 | WATEREE | 2 | 115 |  | Substation | WATEREE PLANT #2 | 115/100 kV Transformer | P3 - CAT1GM - WATERE1001151 | 0 | 101 | 127.3 | 97.1 | 120.2 | 0 | 116.2 | 97.8 | 111.8 | 135.3 | 128.4 | 134.1 | 113.7 | 130.7 | 148.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 98.1 | 114.3 | 148.2 | 3 | 4 | NO |  |  |  | 127.5 | Yes | 1 | No
Contingency Notes:
*Generation Down (e.g. maintenance, etc.)*
CAT1GM: Catawba 1
RBPVGM - Rutabaga PV
MONROE_BJB: Trip Monroe bus junction breaker
BOWATER_YB: Trip Bowater yellow bus (double bus substations label buses red and yellow)
WATERE1001151: Wateree 100 kV / 115 kV Transformer Bank 1
Note on AV19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?
Note on GH4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## Badin
Badin Tie Cluster
[6 empty] | Exclusion Criteria | [5 empty] | Scenario 1 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 2 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 3 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 1 - Winter Cases - Max Branch Loading [%] | [27 empty] | Scenario 2 - Winter Cases - Max Branch Loading [%] | [25 empty] | Scenario 3 - Winter Cases - Max Branch Loading [%] | [29 empty] | 170 | [10 empty] | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Progress Overloads | [11 empty] | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Max Base [%] | Max Overload [%] | Cases with Overloads | [8 empty] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results |  | 190
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Monitored Branch | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_CSM_br1dn | ctpc34s_r3_MVST_Scenario1_CSM_br2dn | ctpc34s_r3_MVST_Scenario1_CSM_hardn | ctpc34s_r3_MVST_Scenario1_CSM_rob2dn | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_SP_br1dn | ctpc34s_r3_MVST_Scenario1_SP_br2dn | ctpc34s_r3_MVST_Scenario1_SP_hardn | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_S90_br1dn | ctpc34s_r3_MVST_Scenario1_S90_br2dn | ctpc34s_r3_MVST_Scenario1_S90_hardn | ctpc34s_r3_MVST_Scenario1_S90_rob2dn | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S110_br1dn | ctpc34s_r3_MVST_Scenario1_S110_br2dn | ctpc34s_r3_MVST_Scenario1_S110_hardn | ctpc34s_r3_MVST_Scenario1_S110_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario1_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario1_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_CSM_br1dn | ctpc34s_r3_MVST_Scenario2_CSM_br2dn | ctpc34s_r3_MVST_Scenario2_CSM_hardn | ctpc34s_r3_MVST_Scenario2_CSM_rob2dn | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_SP_br1dn | ctpc34s_r3_MVST_Scenario2_SP_br2dn | ctpc34s_r3_MVST_Scenario2_SP_hardn | ctpc34s_r3_MVST_Scenario2_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_S90_br1dn | ctpc34s_r3_MVST_Scenario2_S90_br2dn | ctpc34s_r3_MVST_Scenario2_S90_hardn | ctpc34s_r3_MVST_Scenario2_S90_rob2dn | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S110_br1dn | ctpc34s_r3_MVST_Scenario2_S110_br2dn | ctpc34s_r3_MVST_Scenario2_S110_hardn | ctpc34s_r3_MVST_Scenario2_S110_rob2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario2_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario2_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_CSM_br1dn | ctpc34s_r3_MVST_Scenario3_CSM_br2dn | ctpc34s_r3_MVST_Scenario3_CSM_hardn | ctpc34s_r3_MVST_Scenario3_CSM_rob2dn | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_SP_br1dn | ctpc34s_r3_MVST_Scenario3_SP_br2dn | ctpc34s_r3_MVST_Scenario3_SP_hardn | ctpc34s_r3_MVST_Scenario3_SP_rob2dn | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_S90_br1dn | ctpc34s_r3_MVST_Scenario3_S90_br2dn | ctpc34s_r3_MVST_Scenario3_S90_hardn | ctpc34s_r3_MVST_Scenario3_S90_rob2dn | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S110_br1dn | ctpc34s_r3_MVST_Scenario3_S110_br2dn | ctpc34s_r3_MVST_Scenario3_S110_hardn | ctpc34s_r3_MVST_Scenario3_S110_rob2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34s_r3_MVST_Scenario3_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario3_SP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_br1dn | ctpc34w_r3_MVST_Scenario1_WP_br2dn | ctpc34w_r3_MVST_Scenario1_WP_hardn | ctpc34w_r3_MVST_Scenario1_WP_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_waltdn | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W90_br1dn | ctpc34w_r3_MVST_Scenario1_W90_br2dn | ctpc34w_r3_MVST_Scenario1_W90_hardn | ctpc34w_r3_MVST_Scenario1_W90_rob2dn | ctpc34w_r3_MVST_Scenario1_W90_waltdn | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W110_br1dn | ctpc34w_r3_MVST_Scenario1_W110_br2dn | ctpc34w_r3_MVST_Scenario1_W110_hardn | ctpc34w_r3_MVST_Scenario1_W110_rob2dn | ctpc34w_r3_MVST_Scenario1_W110_waltdn | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario1_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario1_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_br1dn | ctpc34w_r3_MVST_Scenario2_WP_br2dn | ctpc34w_r3_MVST_Scenario2_WP_hardn | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W90_br1dn | ctpc34w_r3_MVST_Scenario2_W90_br2dn | ctpc34w_r3_MVST_Scenario2_W90_hardn | ctpc34w_r3_MVST_Scenario2_W90_rob2dn | ctpc34w_r3_MVST_Scenario2_W90_waltdn | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W110_br1dn | ctpc34w_r3_MVST_Scenario2_W110_br2dn | ctpc34w_r3_MVST_Scenario2_W110_hardn | ctpc34w_r3_MVST_Scenario2_W110_rob2dn | ctpc34w_r3_MVST_Scenario2_W110_waltdn | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario2_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_waltdn | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_br1dn | ctpc34w_r3_MVST_Scenario3_WP_br2dn | ctpc34w_r3_MVST_Scenario3_WP_hardn | ctpc34w_r3_MVST_Scenario3_WP_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_waltdn | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W90_br1dn | ctpc34w_r3_MVST_Scenario3_W90_br2dn | ctpc34w_r3_MVST_Scenario3_W90_hardn | ctpc34w_r3_MVST_Scenario3_W90_rob2dn | ctpc34w_r3_MVST_Scenario3_W90_waltdn | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W110_br1dn | ctpc34w_r3_MVST_Scenario3_W110_br2dn | ctpc34w_r3_MVST_Scenario3_W110_hardn | ctpc34w_r3_MVST_Scenario3_W110_rob2dn | ctpc34w_r3_MVST_Scenario3_W110_waltdn | ctpc34w_r3_MVST_Scenario3_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario3_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_waltdn | Total | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
304342,339001,1 | 304342 | BADIN #1 | 339001 | BADIN | 1 | 115 | 304342 BADIN #1 115 339001 BADIN 100 1 | Substation | Badin Transformer 115kV/100kV #1 | 115/100 kV Transformer | TILLERY-PLANT-ALCOA-BADIN-115KV-BLACK-LINE | 126.75 | 100.17 | 100.28 | 95.15 | 101.44 | 126.06 | 99.62 | 99.72 | 94.83 | 133.47 | 106.68 | 106.79 | 101.96 | 107.85 | 146.04 | 119.55 | 119.67 | 114.6 | 120.88 | 173.98 | 147.66 | 147.78 | 142.58 | 149.02 | 100.87 | 138.64 | 113.61 | 113.72 | 108.2 | 114.85 | [10 empty] | 96.5 |  |  |  |  | 116.81 | 92.34 | 92.5 |  | 93.58 | 180.86 | 155.57 | 155.69 | 150.69 | 156.79 | 137.45 | 112.42 | 112.53 | 107.5 | 113.67 | 130.45 | 104.91 | 105.02 | 100.11 | 106.08 | 150.48 | 125.64 | 125.75 | 120.35 | 126.95 | 156.31 | 132.5 | 132.61 | 126.79 | 133.71 | 109.54 | 108.47 |  |  |  |  | 108.27 | 111.11 | 110.11 |  |  |  |  | 110 | 117.19 | 116.04 | 90.97 | 91.01 |  | 92.39 | 115.85 | 149.58 | 148.42 | 123.9 | 123.99 | 118.96 | 125.27 | 148.25 | [28 empty] | 96.39 | 95.21 |  |  |  |  | 95.06 | 98.85 | 97.7 |  |  |  |  | 97.59 | 113.03 | 111.85 |  |  |  |  | 111.78 | 122.66 | 121.48 | 97.79 | 97.89 | 93.07 | 99.26 | 121.32 | 137.45 | 180.86 | 21 | 6 | 25 | 10 | 0 | 6 | 31 | 6 | 31 | 3 | 23 | YES |  |  | 132.99 | 653.9 | TBD | 3 | No
304343,339001,1 | 304343 | BADIN #2 | 339001 | BADIN | 1 | 115 | 304343 BADIN #2 115 339001 BADIN 100 1 | Substation | Badin Transformer 115kV/100kV #2 | 115/100 kV Transformer | TILLERY-PLANT-ALCOA-BADIN-115KV-WHITE-LINE | 120.39 | 95.67 | 95.77 | 90.84 | 96.92 | 119.63 | 94.38 | 94.47 |  | 126.62 | 100.81 | 100.91 | 96.31 | 101.93 | 139.4 | 113.62 | 113.74 | 108.93 | 114.87 | 166.19 | 140.56 | 140.68 | 135.73 | 141.85 | 95.58 | 132.53 | 107.66 | 107.77 | 102.74 | 108.88 | [10 empty] | 93.5 |  |  |  |  | 112.33 |  |  |  |  | 172.31 | 147.54 | 147.65 | 142.78 | 148.73 | 132.25 | 107.63 | 107.73 | 102.97 | 108.81 | 123.89 | 99.06 | 99.17 | 94.42 | 100.2 | 144.47 | 119.72 | 119.83 | 114.82 | 120.95 | 149.82 | 125.36 | 125.48 | 120.24 | 126.54 | 105.99 | 104.97 |  |  |  |  | 104.78 | 106.7 | 105.68 |  |  |  |  | 105.57 | 113.06 | 111.99 |  |  |  |  | 111.82 | 143.8 | 142.74 | 119.54 | 119.61 | 114.82 | 120.84 | 142.58 | [28 empty] | 92.58 | 91.48 |  |  |  |  | 91.33 | 94.54 | 93.44 |  |  |  |  | 93.34 | 106.65 | 105.59 |  |  |  |  | 103.36 | 116.72 | 115.67 | 93.78 | 93.88 |  | 95.2 | 115.52 | 132.25 | 172.31 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | YES |  |  | 120.61 | 640.3 | TBD | 3 | No
304004,304342,1 | 304004 | TILLERY115TT | 304342 | BADIN #1 | 1 | 115 | 304004 TILLERY115TT 115 304342 BADIN #1 115 1 | Line | Tillery Plant - Alcoa Badin 115kV Black | 115 kV Line | TILLERY-PLANT-ALCOA-BADIN-115KV-BLACK-LINE | 124.19 | 97.94 | 98.06 | 93.03 | 99.18 | 123.47 | 97.56 | 97.66 | 92.87 | 130.64 | 104.36 | 104.47 | 99.74 | 105.51 | 143.33 | 117.14 | 117.26 | 112.28 | 118.45 | 170.78 | 144.67 | 144.79 | 139.67 | 146.01 | 98.79 | 135.97 | 111.11 | 111.22 | 105.84 | 112.34 | [10 empty] | 95.08 |  |  |  |  | 114.89 | 90.57 | 90.73 |  | 91.79 | 176.87 | 151.47 | 151.59 | 146.7 | 152.7 | 135.62 | 110.46 | 110.57 | 105.62 | 111.68 | 127.74 | 102.53 | 102.64 | 97.83 | 103.68 | 148.22 | 123.12 | 123.23 | 117.95 | 124.4 | 153.63 | 129.37 | 129.48 | 123.85 | 130.56 | 108.03 | 106.96 |  |  |  |  | 106.76 | 109.16 | 108.15 |  |  |  |  | 108.04 | 115.76 | 114.61 |  |  |  | 91.13 | 114.43 | 148.16 | 146.97 | 122.23 | 122.31 | 117.31 | 123.58 | 146.79 | [28 empty] | 95.49 | 94.29 |  |  |  |  | 94.14 | 97.33 | 96.15 |  |  |  |  | 96.04 | 111.52 | 110.33 |  |  |  |  | 110.14 | 121.78 | 120.62 | 96.83 | 96.94 | 92.2 | 98.29 | 120.46 | 135.62 | 176.87 | 16 | 6 | 24 | 10 | 0 | 6 | 26 | 6 | 30 | 3 | 20 | YES |  |  |  | 653.9 | Yes | 2 | No
304004,304343,1 | 304004 | TILLERY115TT | 304343 | BADIN #2 | 1 | 115 | 304004 TILLERY115TT 115 304343 BADIN #2 115 1 | Line | Tillery Plant - Alcoa Badin 115kV White | 115 kV Line | TILLERY-PLANT-ALCOA-BADIN-115KV-WHITE-LINE | 120.66 | 95.52 | 95.63 | 90.7 | 96.79 | 119.97 | 94.51 | 94.61 |  | 126.91 | 100.85 | 100.96 | 96.34 | 101.99 | 140.37 | 114.06 | 114.18 | 109.34 | 115.32 | 167.59 | 141.31 | 141.43 | 136.43 | 142.61 | 95.73 | 133.26 | 107.61 | 107.73 | 102.85 | 108.86 | [10 empty] | 94.43 |  |  |  |  | 113.25 |  |  |  |  | 172.59 | 146.65 | 146.77 | 141.9 | 147.88 | 133.66 | 108.06 | 108.17 | 103.38 | 109.25 | 124.06 | 98.89 | 99 | 94.21 | 100.02 | 145.9 | 120.01 | 120.13 | 115.18 | 121.17 | 150.97 | 125.12 | 125.24 | 120.23 | 126.32 | 107.12 | 106.03 |  |  |  |  | 105.84 | 107.22 | 106.19 |  |  |  |  | 106.07 | 114.58 | 113.48 |  |  |  | 90.76 | 113.3 | 146.02 | 144.88 | 120.88 | 120.95 | 116.08 | 122.21 | 144.71 | [28 empty] | 93.97 | 92.81 |  |  |  |  | 92.67 | 95.31 | 94.15 |  |  |  |  | 94.05 | 107.7 | 106.62 |  |  |  |  | 105.18 | 118.64 | 117.55 | 95.08 | 95.18 |  | 96.53 | 117.39 | 133.66 | 172.59 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | YES |  |  |  | 677.8 | Yes | 2 | No
304001,304004,1 | 304001 | BLEWETT115TT | 304004 | TILLERY115TT | 1 | 115 | 304001 BLEWETT115TT 115 304004 TILLERY115TT 115 1 | Line | Blewett Falls Plant - Tillery Plant 115kV | 115 kV Line | BISCOE-ROCKINGHAM-230KV-LINE | [9 empty] | 93.48 |  |  |  |  | 110.23 | 97.18 | 97.44 | 105.94 | 93.56 | 119.02 | 106.75 | 106.89 | 115.22 | 102.92 | [41 empty] | 99.02 |  |  | 95.41 | [76 empty] | 99.44 | 98.41 |  |  | 96.13 |  | 98.46 | [7 empty] | 0 | 119.02 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | NO |  |  |  | 76.45 | No | 1 | Yes
[6 empty] | Exclusion Criteria | [5 empty] | Scenario 1 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 2 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 3 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 1 - Winter - Max Branch Loading [%] |  |  |  | Scenario 2 - Winter - Max Branch Loading [%] |  |  |  | Scenario 3 - Winter - Max Branch Loading [%] |  |  |  |  | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Carolinas Overloads | [11 empty] | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Max Loading [%] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage |  | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
309281,339001,1 | 309281 | BADIN W | 339001 | BADIN | 1 | 100 |  | Line | TALLASSEE WH | 100 kV Line | P3 - MCG1GM - TALLASSEEB | 0 | 0 | 222.6 | 0 | 0 | [5 empty] | 108.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 108.1 | 1 | 1 | NO |  |  |  | 88.8 | Yes | 1 | No | Only appears in worse off-peak transfer with P3 contingency
309281,309282,1 | 309281 | BADIN W | 309282 | ALBEMRL2 WH | 1 | 100 |  | Line | TALLASSEE WH | 100 kV Line | P3 - MCG1GM - TALLASSEEB | [10 empty] | 107.7 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 107.7 | 1 | 1 | NO |  |  |  | 88.8 | Yes | 1 | No | Only appears in worse off-peak transfer with P3 contingency
Contingency Notes:
*Generation Down (e.g. maintenance, etc.)*
MCG1GM: McGuire 1
Note on AV13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?
Note on GH4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## Cliffside
DEC - 500 kV to 230 kV or Cliffside Tie Cluster
[6 empty] | Exclusion Criteria |  |  | Exclusion Criteria |  | Scenario 1 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 2 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 3 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 1 - Winter - Max Branch Loading [%] |  |  |  | Scenario 2 - Winter - Max Branch Loading [%] |  |  |  | Scenario 3 - Winter - Max Branch Loading [%] |  |  |  |  | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Carolinas Overloads | [10 empty] | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Max Loading [%] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
306260,308795,1 | 306260 | INMAN | 308795 | CAMPTONW | 1 | 100 | Line | DUNCAN WH N | 100 kV Line | P3 - BUCCGM - NEWPORT_UGBL P2 - DUNCANBN-INM_P21_FS | 0 | 106.4 | 127.5 | 100.7 | 109 | 0 | 120.1 | 117.5 | 100.4 | 125.3 | 0 | 129.5 | 119.4 | 105.4 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6 | 100.6 | 93.9 | 0 | 94.5 | 129.5 | 3 | 4 | NO |  |  |  | 56 | Yes | 1 | No
308494,308795,1 | 308494 | MUDCK R | 308795 | CAMPTONW | 1 | 100 | Line | DUNCAN WH N | 100 kV Line | P3 - WWPVBM - NEWPORT_UGBL P2 - DUNCANBN-INM_P21_FS | 0 | 106.4 | 127.5 | 100.6 | 109 | 0 | 120.1 | 117.5 | 100.3 | 125.3 | 0 | 129.5 | 119.4 | 105.4 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5 | 100.5 | 93.8 | 0 | 94.5 | 129.5 | 3 | 4 | NO |  |  |  | 56 | Yes | 1 | No
306004,306104,1 | 306004 | 6CENTRAL | 306104 | 6SHADYTB | 1 | 230 | Line | FISHER BL | 230 kV Line | P3 - LECCGM - FISHERW P2 - FISHERW-CE_P21 | 0 | 124.6 | 147.7 | 114.9 | 125.6 | 0 | 136.6 | 142.2 | 116.5 | 128.8 | 91.9 | 142.3 | 149.8 | 118.4 | 134.1 | 112.7 | 116.1 | 97.3 | 105.8 | 106 | 112.9 | 102.9 | 110.3 | 111.6 | 115.3 | 96.7 | 105 | 149.8 | 3 | 6 | YES |  |  | 109 | 7119.9 | Yes | 10 | No
306004,306105,2 | 306004 | 6CENTRAL | 306105 | 6SHADYTW | 2 | 230 | Line | FISHER WH | 230 kV Line | P3 - LECCGM - FISHERB P2 - FISHERB-CE_P21 | 0 | 124.6 | 147.7 | 114.9 | 125.6 | 0 | 136.6 | 142.2 | 116.5 | 128.8 | 91.9 | 142.3 | 149.8 | 118.4 | 134.1 | 112.7 | 116.1 | 97.3 | 105.8 | 106 | 112.9 | 102.9 | 110.3 | 111.6 | 115.3 | 96.7 | 105 | 149.8 | 3 | 6 | YES |  |  | 109 | 7119.9 | Yes | 10 | No
306107,306111,1 | 306107 | 6N GRNVLR | 306111 | 6_TIGER | 1 | 230 | Line | FLINT BL | 230 kV Line | P3 - CAT1GM - FLINTW P2 - FLINTW-ETR_P21 | 0 | 117.2 | 146 | 110.9 | 115 | 0 | 130.3 | 133.3 | 112.8 | 129.1 | 0 | 143.9 | 141.2 | 115.3 | 139.2 | 100.3 | 101 | 0 | 96.6 | 0 | 97.1 | 96.9 | 101.2 | 104 | 99.3 | 0 | 96.9 | 146 | 3 | 5 | YES |  |  | 96 | 6298.6 | Yes | 9 | No
306111,309819,2 | 306111 | 6_TIGER | 309819 | 6N GRNVLY | 2 | 230 | Line | FLINT WH | 230 kV Line | P3 - CAT1GM - FLINTB P2 - FLINTB-ETR_P21 | 0 | 117.2 | 146 | 110.9 | 115 | 0 | 130.3 | 133.3 | 112.8 | 129.1 | 0 | 143.9 | 141.2 | 115.3 | 139.2 | 100.3 | 101 | 0 | 96.6 | 0 | 97.1 | 96.9 | 101.2 | 104 | 99.3 | 0 | 96.9 | 146 | 3 | 5 | YES |  |  | 96 | 6298.6 | Yes | 9 | No
306333,306337,A5 | 306333 | 6NEWPORT | 306337 | 8NEWPORT | 5 | 500 | Substation | NEWPORT TIE AT5 | 500/230 kV Transformer | P3 - CAT1GM - MCGUIRE_XFMR P2 - LILESVILLEB-OB_P21 | 102.1 | 139.9 | 162.8 | 120.7 | 142.4 | 102.1 | 144.6 | 171.5 | 130.3 | 166.4 | 135.8 | 183.1 | 171.3 | 154.2 | 190.2 | 110.5 | 127.6 | 100.5 | 130.7 | 103.8 | 126.8 | 99.1 | 124.6 | 137 | 141.7 | 113.6 | 143.6 | 190.2 | 3 | 9 | NO |  |  | 90.5 | 13879.3 | Yes | 15 | No
306333,370020,1 | 306333 | 6NEWPORT | 370020 | 6VCS1-NEWP_P | 1 | 230 | Line | PARR BL | 230 kV Line | P3 - CAT1GM - CAT2 P2 - NEWPORT40P23MB P1 - CAT1 | 155.4 | 172.8 | 197.1 | 170.7 | 187.5 | 155.4 | 146.5 | 139.9 | 139.8 | 168.4 | 149.3 | 145.1 | 140.1 | 146.5 | 151.5 | 102.7 | 103.9 | 99.2 | 116 | 0 | 0 | 0 | 99.6 | 103.5 | 100.8 | 94.8 | 109.2 | 197.1 | 3 | 8 | YES |  |  | 146.2 | 11447.3 | Yes | 14 | No
306111,306236,1 | 306111 | 6_TIGER | 306236 | 6PEACH V | 1 | 230 | Line | PEACH VALLEY BL | 230 kV Line | P3 - CAT1GM - PEACH VALLEY WH P2 - PEACHVW-ETR_P21 | 0 | 95.1 | 122.8 | 0 | 96.5 | 0 | 108.1 | 102.3 | 0 | 105.2 | 0 | 118.2 | 108.4 | 0 | 112.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8 | 3 | 2 | YES |  |  |  | 2132.3 | Yes | 4 | No
306111,306236,2 | 306111 | 6_TIGER | 306236 | 6PEACH V | 2 | 230 | Line | PEACH VALLEY WH | 230 kV Line | P3 - CAT1GM - PEACH VALLEY BL P2 - PEACHVB-ETR_P21 | 0 | 95.1 | 122.8 | 0 | 96.5 | 0 | 108.1 | 102.3 | 0 | 105.2 | 0 | 118.2 | 108.4 | 0 | 112.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8 | 3 | 2 | YES |  |  |  | 2131.5 | Yes | 4 | No
306198,306271,1 | 306198 | TIGER | 306271 | LELIA TP | 1 | 100 | Line | TIGER WH | 100 kV Line | P3 - CAT1GM - PEACHV3C P2 - TIGERB-TIG_P21 | 0 | 104 | 129.9 | 95.9 | 102.1 | 0 | 113.3 | 119.3 | 98.7 | 113.4 | 0 | 133.4 | 135.7 | 108.1 | 132.2 | 115.2 | 117.1 | 101.5 | 112 | 106.8 | 114.9 | 109.9 | 116.9 | 124.3 | 121.5 | 101.7 | 117.2 | 135.7 | 3 | 6 | YES |  |  | 91.7 | 56 | Yes | 3 | No
306113,309002,1 | 306113 | 8JOCASSE | 309002 | 8KATRTRT | 1 | 500 | Line | KATOMA | 500 kV Line | P2 - JOCASSEE55P23MB | [5 empty] | 119.4 | 101.3 | 99.2 | 0 | 0 | 119.3 | 98.5 | 97.9 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4 | 2 | 3 | NO |  |  |  | 2242.8 | Yes | 3 | No
306008,309002,Z1 | 306008 | 8OCONEE | 309002 | 8KATRTRT | 1 | 500 | Line | KATOMA | 500 kV Line | P2 - JOCASSEE55P23MB | [5 empty] | 109.1 | 0 | 0 | 0 | 0 | 109 | 90 | 90.4 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1 | 2 | 2 | NO |  |  |  | 1834 | Yes | 2 | No
Contingency Notes:
*Generation Down (e.g. maintenance, etc.)*
CAT1GM: Catawba 1
LECCGM: Lee CC
BUCCGM: Buck CC
JOCASSEE55P23MB: Middle Breaker (55) at Jocassee trips Foothills and Jocasse Transformer
PEACHV3C (P1-3): Trip Peach Valley Bank 3 and close Bank 1 to pick up the 44 kV
P21: Open one end of a line
Note on AU5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## Woodruff
Woodruff Tie Cluster
[6 empty] | Exclusion Criteria |  |  | Exclusion Criteria |  | Scenario 1 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 2 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 3 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 1 - Winter - Max Branch Loading [%] |  |  |  | Scenario 2 - Winter - Max Branch Loading [%] |  |  |  | Scenario 3 - Winter - Max Branch Loading [%] |  |  |  |  | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Carolinas Overloads | [10 empty] | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Max Loading [%] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
306124,306195,1 | 306124 | BAINBRIG BL | 306195 | SHADY GR | 1 | 100 | Line | BAINBRIDGE BL | 100 kV Line | P2 - OAKVALE_BJB | 149.7 | 153.9 | 159.8 | 149.8 | 156.7 | 173.9 | 128.7 | 132.5 | 125.8 | 130 | 146.9 | 126.5 | 127.8 | 122 | 127.7 | 98.3 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1 | 92.4 | 0 | 0 | 173.9 | 3 | 6 | YES |  |  | 106.1 | 238.9 | Yes | 3 | No
306124,306155,1 | 306124 | BAINBRIG BL | 306155 | GREENVLE | 1 | 100 | Line | BAINBRIDGE BL | 100 kV Line | P2 - OAKVALE_BJB | 127.7 | 127.3 | 128.2 | 127.1 | 130.3 | 151 | 101.9 | 101.5 | 102.9 | 103.2 | 123.6 | 98.5 | 96.5 | 98.6 | 99.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 3 | 5 | NO |  |  |  |  | Yes | 0 | No
306195,309295,1 | 306195 | SHADY GR | 309295 | BAINBRID WH | 1 | 100 | Line | BAINBRIDGE WH | 100 kV Line | P2 - OAKVALE_BJB | 149.7 | 153.9 | 159.8 | 149.8 | 156.7 | 162.9 | 128.7 | 132.5 | 125.8 | 130 | 135.7 | 126.5 | 127.8 | 122 | 127.7 | 98.3 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1 | 91.7 | 0 | 0 | 162.9 | 3 | 6 | YES |  |  | 104.3 | 280.9 | Yes | 3 | No
306155,309295,1 | 306155 | GREENVLE | 309295 | BAINBRID WH | 1 | 100 | Line | BAINBRIDGE WH | 100 kV Line | P2 - OAKVALE_BJB | 141.5 | 143.2 | 145.7 | 130.1 | 146.9 | 162.9 | 118.8 | 116.1 | 116.5 | 118.7 | 135.7 | 113.6 | 113.6 | 109.2 | 114.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.9 | 3 | 6 | YES |  |  | 96.1 | 28 | Yes | 3 | No
306172,306216,1 | 306172 | LAUEC25 | 306216 | LAUEC31 | 1 | 100 | Line | MAULDIN BL | 100 kV Line | P3 - CAT1GM - MAULDINW P2 - CANECRKMAUDW | 126.4 | 144 | 155.9 | 138 | 144 | 126.4 | 127.8 | 134.2 | 121.6 | 129.8 | 107.9 | 130.9 | 132.5 | 120.1 | 131.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3 | 0 | 0 | 0 | 155.9 | 3 | 6 | YES |  |  | 106.8 | 406.9 | Yes | 3 | No
306216,308755,1 | 306216 | LAUEC31 | 308755 | GREENB B | 1 | 100 | Line | MAULDIN BL | 100 kV Line | P3 - CAT1GM - MAULDINW P2 - CANECRKMAUDW | 136.6 | 156.6 | 171.3 | 148.4 | 156.5 | 136.6 | 140.5 | 149.1 | 132.3 | 142.5 | 118.5 | 144.1 | 148 | 131 | 144.6 | 106.8 | 108.7 | 99.4 | 105.5 | 97 | 102.4 | 98.1 | 102.8 | 104.5 | 103.5 | 94 | 98.2 | 171.3 | 3 | 8 | YES |  |  | 117.7 | 890.1 | Yes | 3 | No
306172,308759,1 | 306172 | LAUEC25 | 308759 | LAUEC28B | 1 | 100 | Line | MAULDIN BL | 100 kV Line | P3 - CAT1GM - MAULDINW P2 - CANECRKMAUDW | 95.7 | 106.7 | 111.2 | 106.1 | 107.1 | 95.7 | 0 | 0 | 0 | 0 | 0 | 92.5 | 0 | 0 | 92.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.2 | 1 | 1 | YES |  |  |  |  | No | 1 | No
306133,308765,1 | 306133 | CANE CRK | 308765 | PELHAM B | 1 | 100 | Line | MAULDIN BL | 100 kV Line |  | 0 | 0 | 0 | 0 | 96.8 | [10 empty] | 0 | 0 | 0 | 0 | [8 empty] | 96.8 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
308759,308765,1 | 308759 | LAUEC28B | 308765 | PELHAM B | 1 | 100 | Line | MAULDIN BL | 100 kV Line |  | 0 | 0 | 0 | 0 | 96.8 | [10 empty] | 0 | 0 | 0 | 0 | [8 empty] | 96.8 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306157,308758,1 | 306157 | GREENB W | 308758 | LAUEC25W | 1 | 100 | Line | MAULDIN WH | 100 kV Line | P3 - CAT1GM - MAULDINB P2 - CANECRKMAUDB | 131 | 149.6 | 162.6 | 142.7 | 149.5 | 131 | 133.3 | 140.5 | 126.3 | 135.3 | 112.5 | 136.6 | 139 | 124.9 | 137 | 99.9 | 100.8 | 0 | 98.6 | 0 | 0 | 0 | 96 | 97.5 | 95.6 | 0 | 91.4 | 162.6 | 3 | 6 | YES |  |  | 111.5 | 443.3 | Yes | 3 | No
306173,308758,1 | 306173 | LAUEC28 | 308758 | LAUEC25W | 1 | 100 | Line | MAULDIN WH | 100 kV Line | P3 - CAT1GM - NEWPORT_UGBL P2 - MAULDINB-GB_P21 | 115.6 | 130.5 | 137.7 | 125.1 | 133.7 | 115.6 | 116.7 | 120.3 | 110.3 | 120.5 | 98 | 116.8 | 117.2 | 110.7 | 113.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.7 | 3 | 5 | YES |  |  | 96.8 |  | Yes | 2 | No
306173,306186,1 | 306173 | LAUEC28 | 306186 | PELHAM R | 1 | 100 | Line | MAULDIN WH | 100 kV Line | P2 - MAULDINB-GB_P21 | 100.7 | 111.2 | 116.1 | 104.5 | 115.2 | 100.7 | 98.1 | 0 | 0 | 95.3 | 0 | 94.7 | 95.1 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1 | 2 | 3 | YES |  |  |  |  | Yes | 1 | No
306228,306281,1 | 306228 | WHITMI B | 306281 | MORRIS B | 1 | 100 | Line | MIDWAY BL | 100 kV Line | P2 - BUSHRIV_LT1Y | 171.9 | 175.7 | 183.3 | 174.1 | 186.7 | 172.2 | 134.9 | 138.7 | 130.9 | 143.7 | 148.5 | 154.2 | 156.1 | 144.6 | 160.3 | 108.9 | 110.6 | 105.7 | 116.3 | 0 | 0 | 0 | 0 | 108 | 110.4 | 101.4 | 110.3 | 186.7 | 3 | 8 | YES |  |  | 135.2 | 1114.7 | Yes | 4 | No
306227,306242,1 | 306227 | NEWBER B | 306242 | BUSH RIV | 1 | 100 | Line | MIDWAY BL | 100 kV Line | P3 - CAT1GM - MIDWAYW P2 - BUSHRIV_LT1Y | 113 | 98 | 97.1 | 99 | 98.1 | 113 | 0 | 98.4 | 0 | 103.2 | 112.9 | 108.9 | 111.6 | 100.1 | 114.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1 | 105.3 | 96 | 106.5 | 114.2 | 3 | 5 | YES |  |  | 97.7 | 388.9 | Yes | 3 | No
306227,307881,1 | 306227 | NEWBER B | 307881 | NWBYC5 | 1 | 100 | Line | MIDWAY BL | 100 kV Line | P3 - CAT1GM - SCGP134 P2 - BUSHRIV_LT1Y | 100.1 | 0 | 0 | 0 | 0 | 100.1 | 0 | 0 | 0 | 0 | 105.4 | 101.5 | 103 | 92.7 | 107.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7 | 3 | 4 | YES |  |  |  | 74.4 | No | 2 | No
306228,307881,1 | 306228 | WHITMI B | 307881 | NWBYC5 | 1 | 100 | Line | MIDWAY BL | 100 kV Line | P3 - CAT1GM - SCGP134 | 0 | 95.4 | 95.3 | 95.5 | 95.4 | [5 empty] | 95.9 | 0 | 0 | 0 | 95.8 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 95.9 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306282,306309,1 | 306282 | MORRIS W | 306309 | WHTMR TP | 1 | 100 | Line | MIDWAY WH | 100 kV Line | P2 - MIDWAYB-MOR_P21 | 153.3 | 151.1 | 157.5 | 149.3 | 162.4 | 153.3 | 114.9 | 116.7 | 109.5 | 122.4 | 124.9 | 124.9 | 126.4 | 116.6 | 130.8 | 96.2 | 97.7 | 0 | 102.5 | 0 | 0 | 0 | 0 | 111.6 | 111.1 | 104.9 | 113.9 | 162.4 | 3 | 7 | YES |  |  | 133.7 | 794.2 | Yes | 3 | No
306242,306283,1 | 306242 | BUSH RIV | 306283 | NEWBERRY | 1 | 100 | Line | MIDWAY WH | 100 kV Line | P2 - MIDWAYB-MOR_P21 | 138.8 | 128.8 | 135 | 126.5 | 139.5 | 138.8 | 121.3 | 123.7 | 115.1 | 128.6 | 130.4 | 131 | 133.1 | 122 | 136.7 | 0 | 0 | 0 | 96.6 | 0 | 0 | 0 | 0 | 92.9 | 92.9 | 0 | 95.3 | 139.5 | 3 | 6 | YES |  |  | 104.4 | 425.4 | Yes | 3 | No
306283,306309,1 | 306283 | NEWBERRY | 306309 | WHTMR TP | 1 | 100 | Line | MIDWAY WH | 100 kV Line | P3 - CAT1GM - SCGP134 P2 - MIDWAYB-MOR_P21 | 125.8 | 114.4 | 119.9 | 114.2 | 123.6 | 125.8 | 112.2 | 116.3 | 109.2 | 122.4 | 122.2 | 122.1 | 122.6 | 113.7 | 128.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.7 | 3 | 6 | YES |  |  | 96.1 | 100 | Yes | 3 | No
306278,306286,1 | 306278 | MIDWY TP | 306286 | PACOLET | 1 | 100 | Line | PACWAY BL | 100 kV Line | P2 - PACWAYW-PAC_P21 | 188 | 220.5 | 222.1 | 223.5 | 229.6 | 188 | 127.5 | 126.5 | 129.3 | 134.4 | [5 empty] | 117.1 | 115 | 118.1 | 121.9 | 0 | 0 | 0 | 0 |  |  |  |  | 229.6 | 2 | 5 | NO |  |  | 159.8 | 3013.6 | Yes | 5 | No
306278,306281,1 | 306278 | MIDWY TP | 306281 | MORRIS B | 1 | 100 | Line | PACWAY BL | 100 kV Line | P2 - PACWAYW-PAC_P21 | 132.9 | 137.9 | 141.1 | 138 | 146.3 | 132.9 | 0 | 0 | 0 | 0 | 100.1 | 100.4 | 100 | 95.4 | 104.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.3 | 3 | 5 | NO |  |  |  | 962.4 | Yes | 1 | No
306286,308475,1 | 306286 | PACOLET | 308475 | BRDRV 15 | 1 | 100 | Line | PACWAY WH | 100 kV Line | P2 - PACWAYB-PAC_P21 | 180.1 | 209.7 | 212 | 212.2 | 219.2 | 180.1 | 111.5 | 108.2 | 111.5 | 115.9 | [5 empty] | 112.5 | 110.6 | 112.9 | 117.3 | 0 | 0 | 0 | 0 |  |  |  |  | 219.2 | 2 | 5 | NO |  |  | 111.3 | 2624.1 | Yes | 4 | No
308475,308905,1 | 308475 | BRDRV 15 | 308905 | BRDRV 19 | 1 | 100 | Line | PACWAY WH | 100 kV Line | P2 - PACWAYB-PAC_P21 | 161.6 | 188.1 | 190.5 | 190 | 196.5 | 161.6 | 101.2 | 98.6 | 100.8 | 105.1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 196.5 | 2 | 4 | NO |  |  | 108.4 | 2624.1 | Yes | 4 | No
306282,308801,1 | 306282 | MORRIS W | 308801 | MIDW T W | 1 | 100 | Line | PACWAY WH | 100 kV Line | P2 - PACWAYB-PAC_P21 | 164.2 | 184.7 | 186.4 | 186.9 | 193.5 | 164.2 | 116.4 | 113.7 | 115.6 | 120.8 | 98.9 | 98.8 | 98.4 | 93.9 | 103.2 | 102.6 | 101.2 | 102.8 | 107.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.5 | 3 | 5 | NO |  |  | 117.4 | 2434.3 | Yes | 4 | No
308801,308905,1 | 308801 | MIDW T W | 308905 | BRDRV 19 | 1 | 100 | Line | PACWAY WH | 100 kV Line | P2 - PACWAYB-PAC_P21 | 145.2 | 163.4 | 164.9 | 165.3 | 171.2 | 145.2 | 103 | 100.6 | 102.3 | 106.8 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 171.2 | 2 | 4 | NO |  |  | 110.7 | 1985.1 | Yes | 3 | No
306268,308714,1 | 306268 | LAURENS | 308714 | LAURENC5 | 1 | 100 | Line | RABON BL | 100 kV Line | P2 - RABONW-LEE_P21 | 135.4 | 107.2 | 103.9 | 113.6 | 111.9 | 135.4 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 135.4 | 2 | 3 | NO |  |  |  | 725.7 | Yes | 1 | No
306097,308714,1 | 306097 | LAUEC32 T | 308714 | LAURENC5 | 1 | 100 | Line | RABON BL | 100 kV Line | P2 - RABONW-LEE_P21 | 131.2 | 102.6 | 98 | 109.5 | 106.8 | 131.2 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 131.2 | 2 | 3 | NO |  |  |  | 725.7 | Yes | 1 | No
306041,306097,1 | 306041 | LEE | 306097 | LAUEC32 T | 1 | 100 | Line | RABON BL | 100 kV Line | P2 - RABONW-LEE_P21 | 148.1 | 112 | 108.1 | 119.3 | 117.4 | 148.1 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 148.1 | 2 | 3 | NO |  |  |  | 685.7 | Yes | 1 | No
306041,309167,2 | 306041 | LEE | 309167 | LAUEC42 | 2 | 100 | Line | RABON WH | 100 kV Line | P3 - LECCGM - RABONB P2 - RABONB-LEE_P21 | 194.1 | 154.8 | 152.8 | 155.2 | 161.3 | 194.1 | 0 | 0 | 0 | 0 | 97.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.1 | 2 | 3 | NO |  |  | 109.6 | 2396.7 | Yes | 4 | No
306268,308497,2 | 306268 | LAURENS | 308497 | LAUEC33 | 2 | 100 | Line | RABON WH | 100 kV Line | P3 - LECCGM - RABONB P2 - RABONB-LEE_P21 | 149.9 | 119.3 | 114.9 | 120.7 | 125.7 | 149.9 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 149.9 | 2 | 3 | NO |  |  |  | 885.7 | Yes | 1 | No
308497,309167,2 | 308497 | LAUEC33 | 309167 | LAUEC42 | 2 | 100 | Line | RABON WH | 100 kV Line | P3 - LECCGM - RABONB P2 - RABONB-LEE_P21 | 142.7 | 112.6 | 107.9 | 114.4 | 118.7 | 142.7 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 142.7 | 2 | 3 | NO |  |  |  | 362.8 | Yes | 1 | No
306305,306307,1 | 306305 | W SPTBRG | 306307 | WALDEN T | 1 | 100 | Line | TIGER BL | 100 kV Line | P2 - TIGERW-TI_P21 | 0 | 99.7 | 128.6 | 95.6 | 107.2 | 0 | 124.3 | 117.9 | 99 | 121.2 | 0 | 142.9 | 140.5 | 113.9 | 139.9 | 109.4 | 108.5 | 0 | 100.8 | 101 | 101 | 102.8 | 107.4 | 115.8 | 115.1 | 92.6 | 107.2 | 142.9 | 3 | 5 | NO |  |  | 90.9 | 56 | Yes | 2 | No
306198,306307,1 | 306198 | TIGER | 306307 | WALDEN T | 1 | 100 | Line | TIGER BL | 100 kV Line | P2 - TIGERW-TI_P21 | 0 | 0 | 108.4 | 0 | 0 | 0 | 101.8 | 99.1 | 0 | 95.7 | 0 | 115.1 | 114.8 | 92.7 | 113.6 | 100.3 | 100.2 | 0 | 0 | 0 | 0 | 0 | 98.5 | 105.5 | 105.7 | 0 | 98.4 | 115.1 | 3 | 4 | NO |  |  |  | 56 | No | 1 | No
306198,306271,1 | 306198 | TIGER | 306271 | LELIA TP | 1 | 100 | Line | TIGER WH | 100 kV Line | P3 - CAT1GM - TIGERB P2 - TIGERB_TIG_P21 | 0 | 104 | 129.9 | 95.9 | 102.1 | 0 | 113.3 | 119.3 | 98.7 | 113.4 | 0 | 133.4 | 135.7 | 108.1 | 132.2 | 115.2 | 117.1 | 101.5 | 112 | 106.8 | 114.9 | 109.9 | 116.9 | 124.3 | 121.5 | 101.7 | 117.2 | 135.7 | 3 | 6 | YES |  |  | 91.7 | 56 | Yes | 3 | No
306305,308809,1 | 306305 | W SPTBRG | 308809 | WALDENTW | 1 | 100 | Line | TIGER WH | 100 kV Line | P3 - CAT1GM - NEWPORT_UGBL P2 - TIGERB-TIG_P21 | 0 | 102.8 | 120.1 | 95.2 | 105.2 | 0 | 121.8 | 117.9 | 100.9 | 124 | 0 | 136.7 | 136.6 | 117.2 | 134.4 | 96.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7 | 99.7 | 0 | 94.1 | 136.7 | 3 | 4 | NO |  |  |  | 56 | Yes | 1 | No
306271,308809,1 | 306271 | LELIA TP | 308809 | WALDENTW | 1 | 100 | Line | TIGER WH | 100 kV Line | P3 - CAT1GM - TIGERB | [10 empty] | 0 | 96.2 | 94.3 | 0 | 94.7 | [8 empty] | 0 | 0 | 0 | 0 | 96.2 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
Contingency Notes:
*Generation Down (e.g. maintenance, etc.)*
CAT1GM: Catawba 1
LECCGM: Lee CC
P21: Open one end of a line
SCGP134: Loss of VC Summer to Parr Line?
NEWPORT_UGBL: Loss of Newport Transformer #5 Underground Busline
BUSHRIV_LT1Y: Bush River low tension breaker failure (yellow bus)
Note on AU5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## Harley Hogback
Harley Hogback Cluster
[6 empty] | Exclusion Criteria |  |  | Exclusion Criteria |  | Scenario 1 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 2 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 3 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 1 - Winter - Max Branch Loading [%] |  |  |  | Scenario 2 - Winter - Max Branch Loading [%] |  |  |  | Scenario 3 - Winter - Max Branch Loading [%] |  |  |  |  | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Carolinas Overloads | [10 empty] | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Max Loading [%] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Line or Substation | Branch Name | Branch Type | Worst Contingency | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
307246,307518,1 | 307246 | 1CAMPOBL | 307518 | 1MASCOTR | 1 | 44 | Line | CAMPOBELLO A | 44 kV Line | P2 - CAMPBA-IN-P21 | 0 | 0 | 102.3 | 0 | 0 | 96.8 | 0 | 100.9 | 0 | 0 | 97.3 | 92 | 105.5 | 0 | 91.8 | 112.8 | 131.9 | 95.1 | 112 | 109.4 | 129.8 | 0 | 111.2 | 112 | 131.8 | 94.3 | 111.5 | 131.9 | 3 | 3 | YES |  |  |  |  | Yes | 1 | Yes
307479,307481,1 | 307479 | 1INMAN | 307481 | 1INMAN S | 1 | 44 | Line | CAMPOBELLO A | 44 kV Line | P2 - CAMPOBEL_BJB | 0 | 0 | 98.4 | 0 | 0 | 0 | 0 | 96.7 | 0 | 0 | 144.8 | 102.7 | 109.1 | 94.1 | 102.4 | 116 | 129.8 | 101.5 | 114.8 | 111.9 | 128.6 | 96.1 | 115.6 | 115.6 | 129.7 | 101.3 | 114.9 | 144.8 | 3 | 5 | YES |  |  |  |  | Yes | 1 | Yes
307481,307518,1 | 307481 | 1INMAN S | 307518 | 1MASCOTR | 1 | 44 | Line | CAMPOBELLO A | 44 kV Line | P2 - CAMPOBEL_BJB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.4 | 95.8 | 101.8 | 0 | 95.3 | 111.5 | 125 | 97.3 | 110.3 | 107.5 | 124.3 | 0 | 111.1 | 111.1 | 124.9 | 97.1 | 110.4 | 138.4 | 3 | 4 | YES |  |  |  |  | Yes | 1 | Yes
307411,307478,1 | 307411 | 1BRDRV 4 | 307478 | 1INTWIRET | 1 | 44 | Line | CAMPOBELLO B | 44 kV Line | P2 - CAMPOBEL_BJB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.9 | 0 | 0 | 0 | 0 | 0 | 97.8 | 0 | 0 | 0 | 97.4 | 0 | 0 | 0 | 97.7 | 0 | 0 | 107.9 | 1 | 1 | NO |  |  |  |  | No | 0 | Yes
307411,307479,1 | 307411 | 1BRDRV 4 | 307479 | 1INMAN | 1 | 44 | Line | CAMPOBELLO B | 44 kV Line | P2 - CAMPOBEL_BJB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3 | 0 | 0 | 0 | 0 | 0 | 97.8 | 0 | 0 | 0 | 97.4 | 0 | 0 | 0 | 97.7 | 0 | 0 | 108.3 | 1 | 1 | NO |  |  |  |  | Yes | 0 | Yes
307478,307480,1 | 307478 | 1INTWIRET | 307480 | 1INMAN 2 | 1 | 44 | Line | CAMPOBELLO B | 44 kV Line | P2 - CAMPOBEL_BJB | [10 empty] | 99.6 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 91.8 | 0 | 0 | 99.6 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | Yes
306120,306163,1 | 306120 | ASHVL HW | 306163 | HNDRSNVL | 1 | 100 | Line | ECHO BL | 100 kV Line | P2 - ECHOW-HOR_P21 | 0 | 0 | 103.8 | 0 | 0 | 0 | 0 | 101.9 | 0 | 0 | 0 | 90.5 | 104.9 | 0 | 90 | 106 | 128.2 | 0 | 105.3 | 103.3 | 125.9 | 0 | 104.6 | 105.5 | 127.9 | 0 | 104.8 | 128.2 | 3 | 3 | YES | 95.7 | 98.5 |  |  | No | 3 | No
306164,308471,1 | 306164 | HORSESHO | 308471 | NIXRDTAP | 1 | 100 | Line | ECHO BL | 100 kV Line | P2 - ECHOW-HOR_P21 | 0 | 0 | 104.9 | 0 | 0 | 0 | 0 | 101.2 | 0 | 0 | 0 | 107.9 | 119.3 | 0 | 106.9 | 109.6 | 123.5 | 0 | 107.9 | 101.6 | 120.2 | 0 | 107.5 | 110.1 | 126.9 | 0 | 108.8 | 126.9 | 3 | 4 | YES |  |  |  |  | Yes | 1 | No
306164,308740,1 | 306164 | HORSESHO | 308740 | ASHVHWYW | 1 | 100 | Line | ECHO WH | 100 kV Line | P2 - ECHOB-HOR_P21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4 | 106.6 | 0 | 96.1 | 98.6 | 113.9 | 0 | 96.7 | 0 | 110.1 | 0 | 96 | 98.8 | 117.3 | 0 | 97.4 | 117.3 | 3 | 0 | YES |  |  |  |  | Yes | 1 | No
306171,308740,1 | 306171 | UPWARDRD | 308740 | ASHVHWYW | 1 | 100 | Line | ECHO WH | 100 kV Line | P2 - ECHOB-HOR_P21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4 | 106.6 | 0 | 94.3 | 98.5 | 113.9 | 0 | 96.7 | 0 | 110.1 | 0 | 96 | 98.7 | 117.2 | 0 | 97.4 | 117.2 | 3 | 0 | YES |  |  |  |  | No | 1 | No
306198,308709,2 | 306198 | TIGER | 308709 | NEWCUTRET | 2 | 100 | Line | HARLEY BL | 100 kV Line | P2 - HARLEYW_P21 | 0 | 98.8 | 112.5 | 0 | 101.2 | 0 | 106.4 | 106.8 | 0 | 98.3 | 0 | 117.5 | 121.6 | 105.6 | 114.2 | 124.8 | 136.5 | 110.5 | 119.3 | 122.8 | 135.2 | 112.6 | 123.4 | 123.4 | 137.9 | 109.3 | 120.2 | 137.9 | 3 | 5 | YES | 103.6 | 103.3 |  |  | Yes | 3 | Conceptual
306132,308709,2 | 306132 | CAMPOBEL | 308709 | NEWCUTRET | 2 | 100 | Line | HARLEY BL | 100 kV Line | P2 - HARLEYW_P21 | 0 | 0 | 100.6 | 0 | 0 | 0 | 95.6 | 0 | 0 | 0 | 0 | 105.5 | 108.3 | 95.5 | 102.2 | 110.3 | 119.5 | 98.2 | 104.8 | 108.6 | 118.4 | 100.3 | 108.9 | 108.8 | 120.9 | 96.9 | 105.6 | 120.9 | 3 | 4 | YES |  |  | 105.5 |  | Yes | 2 | Conceptual
306132,306198,1 | 306132 | CAMPOBEL | 306198 | TIGER | 1 | 100 | Line | HARLEY WH | 100 kV Line | P2 - HARLEYB-TIG_P21 | 0 | 96.7 | 110.2 | 0 | 99.1 | 0 | 104.3 | 104.4 | 0 | 95.6 | 0 | 114.6 | 119 | 103.7 | 109.9 | 122.1 | 133.5 | 108.2 | 116.7 | 120.1 | 132.2 | 110.4 | 120.8 | 120.8 | 134.9 | 107 | 117.5 | 134.9 | 3 | 5 | YES | 101.2 | 100.8 | 111.5 |  | Yes | 4 | Conceptual
306163,309312,Z1 | 306163 | HNDRSNVL | 309312 | HNDRSNV2 | 1 | 100 | Substation | HENDERSONVILLE TIE | 100/44 kV - 100 kV Breaker | P2 - TUX44A-CA-P21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3 | 0 | 0 | 0 | 103.9 | 0 | 0 | 92.9 | 106.3 | 0 | 92.3 | 106.3 | 3 | 0 | YES |  |  |  |  | No | 1 | No
307283,309312,3 | 307283 | 1HNDRSNV | 309312 | HNDRSNV2 | 3 | 100 | Substation | HENDERSONVILLE TIE 03 | 100/44 kV Transformer | P3 - TUXDGM - HENDBK2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 100.9 | 0 | 0 | 100.9 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
306132,307053,2 | 306132 | CAMPOBEL | 307053 | BREC32 | 2 | 100 | Line | HOGBACK BL | 100 kV Line | P2 - HOGBACKW_P21 | 106.7 | 0 | 0 | 0 | 0 | 106.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8 | 0 | 0 | 0 | 101.3 | 0 | 0 | 0 | 98.5 | 0 | 0 | 106.7 | 2 | 2 | NO | 96.9 | 103.7 |  | 130 | Yes | 3 | Conceptual
306163,307053,2 | 306163 | HNDRSNVL | 307053 | BREC32 | 2 | 100 | Line | HOGBACK BL | 100 kV Line | P2 - HOGBACKW_P21 | 104.3 | 0 | 0 | 0 | 0 | 104.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2 | 0 | 0 | 0 | 97.7 | 0 | 0 | 0 | 94.9 | 0 | 0 | 104.3 | 2 | 2 | NO | 107.6 | 100.8 |  |  | No | 2 | Conceptual
306132,306163,1 | 306132 | CAMPOBEL | 306163 | HNDRSNVL | 1 | 100 | Line | HOGBACK WH | 100 kV Line | P2 - HOGBACKB-CA_P21 | 105.6 | 0 | 0 | 0 | 0 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 98.6 | 0 | 0 | 0 | 95.7 | 0 | 0 | 105.6 | 2 | 2 | NO | 95.2 | 106.6 |  | 130 | Yes | 3 | Conceptual
306101,309313,1 | 306101 | 3HORSESH | 309313 | HORSES1&2 | 1 | 115 | Substation | HORSESHOE TIE 01 | 115/100 kV Transformer | P2 - RUGBYW-PIS_P21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 113.4 | 0 | 96.5 | 0 | 110.6 | 0 | 0 | 97.4 | 116.9 | 0 | 97.8 | 116.9 | 3 | 0 | YES |  |  |  |  | Yes | 1 | No
307246,307304,1 | 307246 | 1CAMPOBL | 307304 | 1LANDRUM | 1 | 44 | Line | TUXEDO A | 44 kV Line | P2 - HNDRSNVL_HT | 121.6 | 130 | 152.4 | 115.7 | 129.3 | 173.8 | 127.4 | 145.5 | 115.8 | 128.6 | 176.6 | 120.9 | 133.7 | 0 | 120.8 | 134.8 | 155.9 | 113.9 | 134.2 | 128.7 | 154.9 | 112.8 | 133.2 | 133.2 | 155.2 | 112.4 | 133.1 | 176.6 | 3 | 9 | YES |  |  |  | 140 | Yes | 2 | No
307344,307355,1 | 307344 | 1SALUDAA | 307355 | 1TUXEDO | 1 | 44 | Line | TUXEDO A | 44 kV Line | P2 - TUX44A-CA-P21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.6 | 176 | 113.8 | 140.4 | 133.7 | 172.4 | 112.1 | 139.3 | 140.2 | 175.1 | 112.2 | 139.5 | 176 | 3 | 3 | YES |  |  |  |  | No | 1 | No
308582,308583,1 | 308582 | 1TRYONA | 308583 | 1SJOHN TA | 1 | 44 | Line | TUXEDO A | 44 kV Line | P2 - HNDRSNVL_RB | 0 | 0 | 0 | 0 | 0 | 118.2 | 0 | 0 | 0 | 0 | 119.7 | 0 | 0 | 0 | 0 | 0 | 119.1 | 0 | 0 | 0 | 116.8 | 0 | 0 | 93.8 | 118.3 | 0 | 93.4 | 119.7 | 3 | 2 | YES |  |  |  |  | Yes | 1 | No
307304,308583,1 | 307304 | 1LANDRUM | 308583 | 1SJOHN TA | 1 | 44 | Line | TUXEDO A | 44 kV Line | P2 - HNDRSNVL_RB | 0 | 0 | 0 | 0 | 0 | 118.2 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 117.7 | 0 | 0 | 0 | 115.6 | 0 | 0 | 93.1 | 116.9 | 0 | 92.7 | 120 | 3 | 2 | YES |  |  |  |  | Yes | 1 | No
307246,307343,1 | 307246 | 1CAMPOBL | 307343 | 1SJOHN TB | 1 | 44 | Line | TUXEDO B | 44 kV Line | P2 - HNDRSNVL_RB | 106.5 | 113.8 | 124.2 | 100.9 | 110.8 | 150.9 | 108.3 | 114.5 | 100.8 | 109.6 | 153.3 | 0 | 98.1 | 0 | 0 | 107.4 | 128.3 | 0 | 107 | 99 | 126.8 | 0 | 106.4 | 105.7 | 125.5 | 0 | 105.8 | 153.3 | 3 | 7 | YES |  |  |  | 70 | Yes | 2 | No
307343,307598,1 | 307343 | 1SJOHN TB | 307598 | 1TRYONB | 1 | 44 | Line | TUXEDO B | 44 kV Line | P2 - HNDRSNVL_RB | 105.9 | 113.2 | 123.2 | 100.4 | 110.2 | 150.8 | 107.7 | 113.8 | 100.3 | 109 | 152.5 | 0 | 97.5 | 0 | 0 | 106.9 | 127.6 | 0 | 106.6 | 98.7 | 126.2 | 0 | 106 | 105.2 | 124.8 | 0 | 105.4 | 152.5 | 3 | 7 | YES |  |  |  | 70 | Yes | 2 | No
Contingency Notes:
*Generation Down (e.g. maintenance, etc.)*
TUXDGM: Tuxedo Hydro
P21: Open one end of a line
CAMPOBEL_BJB: Trip Campobello bus junction breaker
HNDRSNVL_HT: Hendersonville Tie high tension breaker failure
HNDRSNVL_RB: Trip Hendersonville Mn red bus (double bus substations label buses red and yellow)
Note on AU5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## Other->
Other Clusters Notes
Other Clusters have been reviewed but are tied to specific generator resources that will drive the timing of needs
These clusters will inform decision making in other planning processes and future MVST studies
Worst contingencies have not been listed for these clusters but is available in the overall Needs results on the SFTP

## NewBernOFW
New Bern OFW Cluster
| Exclusion Criteria |  |  |  | Scenario 1 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 2 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 3 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 1 - Winter Cases - Max Branch Loading [%] | [27 empty] | Scenario 2 - Winter Cases - Max Branch Loading [%] | [25 empty] | Scenario 3 - Winter Cases - Max Branch Loading [%] | [29 empty] | 170 | [10 empty] | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Progress Overloads |  |  |  |  | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Max Base [%] | Max Overload [%] | Cases with Overloads | [8 empty] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results |  | 190
Branch Identifier | Voltage | Monitored Branch | Line or Substation | Branch Name | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_CSM_br1dn | ctpc34s_r3_MVST_Scenario1_CSM_br2dn | ctpc34s_r3_MVST_Scenario1_CSM_hardn | ctpc34s_r3_MVST_Scenario1_CSM_rob2dn | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_SP_br1dn | ctpc34s_r3_MVST_Scenario1_SP_br2dn | ctpc34s_r3_MVST_Scenario1_SP_hardn | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_S90_br1dn | ctpc34s_r3_MVST_Scenario1_S90_br2dn | ctpc34s_r3_MVST_Scenario1_S90_hardn | ctpc34s_r3_MVST_Scenario1_S90_rob2dn | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S110_br1dn | ctpc34s_r3_MVST_Scenario1_S110_br2dn | ctpc34s_r3_MVST_Scenario1_S110_hardn | ctpc34s_r3_MVST_Scenario1_S110_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario1_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario1_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_CSM_br1dn | ctpc34s_r3_MVST_Scenario2_CSM_br2dn | ctpc34s_r3_MVST_Scenario2_CSM_hardn | ctpc34s_r3_MVST_Scenario2_CSM_rob2dn | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_SP_br1dn | ctpc34s_r3_MVST_Scenario2_SP_br2dn | ctpc34s_r3_MVST_Scenario2_SP_hardn | ctpc34s_r3_MVST_Scenario2_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_S90_br1dn | ctpc34s_r3_MVST_Scenario2_S90_br2dn | ctpc34s_r3_MVST_Scenario2_S90_hardn | ctpc34s_r3_MVST_Scenario2_S90_rob2dn | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S110_br1dn | ctpc34s_r3_MVST_Scenario2_S110_br2dn | ctpc34s_r3_MVST_Scenario2_S110_hardn | ctpc34s_r3_MVST_Scenario2_S110_rob2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario2_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario2_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_CSM_br1dn | ctpc34s_r3_MVST_Scenario3_CSM_br2dn | ctpc34s_r3_MVST_Scenario3_CSM_hardn | ctpc34s_r3_MVST_Scenario3_CSM_rob2dn | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_SP_br1dn | ctpc34s_r3_MVST_Scenario3_SP_br2dn | ctpc34s_r3_MVST_Scenario3_SP_hardn | ctpc34s_r3_MVST_Scenario3_SP_rob2dn | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_S90_br1dn | ctpc34s_r3_MVST_Scenario3_S90_br2dn | ctpc34s_r3_MVST_Scenario3_S90_hardn | ctpc34s_r3_MVST_Scenario3_S90_rob2dn | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S110_br1dn | ctpc34s_r3_MVST_Scenario3_S110_br2dn | ctpc34s_r3_MVST_Scenario3_S110_hardn | ctpc34s_r3_MVST_Scenario3_S110_rob2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34s_r3_MVST_Scenario3_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario3_SP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_br1dn | ctpc34w_r3_MVST_Scenario1_WP_br2dn | ctpc34w_r3_MVST_Scenario1_WP_hardn | ctpc34w_r3_MVST_Scenario1_WP_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_waltdn | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W90_br1dn | ctpc34w_r3_MVST_Scenario1_W90_br2dn | ctpc34w_r3_MVST_Scenario1_W90_hardn | ctpc34w_r3_MVST_Scenario1_W90_rob2dn | ctpc34w_r3_MVST_Scenario1_W90_waltdn | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W110_br1dn | ctpc34w_r3_MVST_Scenario1_W110_br2dn | ctpc34w_r3_MVST_Scenario1_W110_hardn | ctpc34w_r3_MVST_Scenario1_W110_rob2dn | ctpc34w_r3_MVST_Scenario1_W110_waltdn | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario1_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario1_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_br1dn | ctpc34w_r3_MVST_Scenario2_WP_br2dn | ctpc34w_r3_MVST_Scenario2_WP_hardn | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W90_br1dn | ctpc34w_r3_MVST_Scenario2_W90_br2dn | ctpc34w_r3_MVST_Scenario2_W90_hardn | ctpc34w_r3_MVST_Scenario2_W90_rob2dn | ctpc34w_r3_MVST_Scenario2_W90_waltdn | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W110_br1dn | ctpc34w_r3_MVST_Scenario2_W110_br2dn | ctpc34w_r3_MVST_Scenario2_W110_hardn | ctpc34w_r3_MVST_Scenario2_W110_rob2dn | ctpc34w_r3_MVST_Scenario2_W110_waltdn | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario2_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_waltdn | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_br1dn | ctpc34w_r3_MVST_Scenario3_WP_br2dn | ctpc34w_r3_MVST_Scenario3_WP_hardn | ctpc34w_r3_MVST_Scenario3_WP_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_waltdn | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W90_br1dn | ctpc34w_r3_MVST_Scenario3_W90_br2dn | ctpc34w_r3_MVST_Scenario3_W90_hardn | ctpc34w_r3_MVST_Scenario3_W90_rob2dn | ctpc34w_r3_MVST_Scenario3_W90_waltdn | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W110_br1dn | ctpc34w_r3_MVST_Scenario3_W110_br2dn | ctpc34w_r3_MVST_Scenario3_W110_hardn | ctpc34w_r3_MVST_Scenario3_W110_rob2dn | ctpc34w_r3_MVST_Scenario3_W110_waltdn | ctpc34w_r3_MVST_Scenario3_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario3_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_waltdn | Total | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
304445,304451,1 | 230 | 304445 CHOCOWINITY 230 304451 GREENVILE TT 230 1 | Line | Aurora SS - Greenville 230kV | 162.98 | 135.76 | 137.19 | 151.06 | 147.11 | 120.9 | 100.17 | 101.19 | 110.21 | 129.39 | 106.51 | 107.53 | 116.65 | 112.94 | 121.85 | 98.58 | 99.61 | 109.32 | 105.94 | 160.76 | 129.9 | 130.05 | 145.42 | 140.74 | 106.78 | 156.55 | 128.3 | 129.71 | 143.38 | 139.21 | 116.17 | 94.8 | 95.99 | 105.03 | 101.44 | 123.23 | 100.65 | 101.79 | 110.91 | 107.05 | 113.89 | 93.33 | 94.35 | 103.51 | 99.97 | 152.08 | 121.07 | 121.2 | 136.43 | 131.39 | 157.55 | 130.67 | 131.79 | 144.89 | 141.2 | 119.57 | 99.2 | 100.21 | 109.41 | 106.06 | 126.27 | 105.08 | 106.13 | 115.25 | 111.76 | 127.59 | 103.27 | 104.37 | 115.09 | 111.4 | 163.15 | 129.57 | 129.86 | 146.92 | 141.34 | 91.61 | 91.57 |  |  |  |  | 91.59 | 98.94 | 98.89 |  |  |  |  | 98.91 | 91.17 | 91.08 |  |  |  |  | 91.13 | 117.91 | 117.83 | 96.96 | 97.02 | 107.25 | 104.34 | 117.87 | [5 empty] | 96.84 | 96.8 |  |  |  |  | 96.82 | [7 empty] | 116.03 | 115.95 | 94.15 | 94.19 | 104.81 | 101.33 | 115.99 |  |  | 97.74 | 97.65 |  |  |  |  | 97.69 | 106.15 | 106.06 |  |  | 95.59 | 92.6 | 106.1 | 99.38 | 99.28 |  |  |  |  | 99.34 | 121.21 | 121.12 | 98.12 | 98.33 | 110.46 | 107.22 | 121.15 | 120.9 | 163.15 | 23 | 20 | 24 | 5 | 5 | 5 | 28 | 25 | 29 | 3 | 26 | NO |  |  |  | 8688.06 | Yes | 9 | No
304449,304473,1 | 230 | 304449 EDWARDS TAP 230 304473 PA-WASHINTON 230 1 | Line | Aurora SS - Greenville 230kV | 153.71 | 129.15 | 130.47 | 143.13 | 139.59 | 122.39 | 103.46 | 104.42 | 112.79 | 128.45 | 107.37 | 108.32 | 116.78 | 113.41 | 125.56 | 104.05 | 105 | 114.23 | 111.4 | 159.77 | 131.18 | 131.32 | 145.68 | 141.36 | 109.68 | 147.78 | 122.36 | 123.67 | 136.13 | 132.41 | 118.01 | 98.56 | 99.67 | 108.07 | 104.79 | 122.54 | 101.99 | 103.05 | 111.49 | 108 | 117.99 | 99.24 | 100.18 | 108.7 | 105.47 | 151.65 | 122.92 | 123.05 | 137.34 | 132.68 | 148.72 | 124.34 | 125.38 | 137.47 | 134.18 | 121.18 | 102.56 | 103.5 | 112.05 | 109 | 125.36 | 106.02 | 106.99 | 115.46 | 112.3 | 130.93 | 108.41 | 109.43 | 119.6 | 116.22 | 162.09 | 130.88 | 131.16 | 147.14 | 141.95 | 95.89 | 95.85 |  |  |  |  | 95.87 | 100.83 | 100.79 |  |  | 92.57 |  | 100.8 | 97.35 | 97.27 |  |  |  |  | 97.31 | 119.77 | 119.7 | 100.75 | 100.8 | 110.06 | 107.43 | 119.74 | 94.11 | 94.06 |  |  |  | 98.91 | 98.87 |  |  |  |  | 98.89 | 94.98 | 94.9 |  |  |  |  | 94.95 | 118.04 | 117.96 | 98.17 | 98.21 | 107.85 | 104.66 | 118 |  | 94.08 | 101.47 | 101.38 |  |  | 93.95 | 91.44 | 101.43 | 107.3 | 107.23 |  | 90.55 | 97.86 | 95.15 | 107.26 | 104.82 | 104.73 |  |  | 96.26 | 93.7 | 104.78 | 122.84 | 122.75 | 101.8 | 101.99 | 113.02 | 110.06 | 122.77 | 122.39 | 162.09 | 25 | 22 | 25 | 7 | 5 | 10 | 32 | 27 | 35 | 3 | 30 | NO |  |  |  | 8688.06 | Yes | 9 | No
304445,304473,1 | 230 | 304445 CHOCOWINITY 230 304473 PA-WASHINTON 230 1 | Line | Aurora SS - Greenville 230kV | 148.03 | 123.27 | 124.58 | 137.32 | 133.77 | 113.29 | 94.3 | 95.25 | 103.58 | 120.57 | 99.59 | 100.53 | 108.95 | 105.57 | 114.82 | 93.44 | 94.38 | 103.4 | 100.36 | 150.21 | 121.81 | 121.94 | 136.16 | 131.87 | 100.46 | 142.13 | 116.44 | 117.74 | 130.32 | 126.55 | 108.92 |  | 90.47 | 98.82 | 95.54 | 114.85 | 94.19 | 95.25 | 103.66 | 100.15 | 107.43 |  |  | 98.01 | 94.78 | 142.17 | 113.64 | 113.76 | 127.85 | 123.23 | 143.07 | 118.6 | 119.63 | 131.68 | 128.34 | 112.06 | 93.4 | 94.34 | 102.84 | 99.78 | 117.65 | 98.25 | 99.22 | 107.64 | 104.47 | 120.13 | 97.77 | 98.79 | 108.73 | 105.35 | 152.43 | 121.5 | 121.76 | 137.55 | 132.43 | [7 empty] | 92.16 | 92.11 |  |  |  |  | 92.13 | [7 empty] | 109.71 | 109.64 | 90.9 | 90.96 | 100.13 | 97.52 | 109.68 | [5 empty] | 90.27 | 90.23 |  |  |  |  | 90.25 | [7 empty] | 108.02 | 107.95 |  |  | 97.94 | 94.81 | 107.98 |  |  | 91.6 | 91.52 |  |  |  |  | 91.56 | 98.61 | 98.54 |  |  |  |  | 98.57 | 93.64 | 93.55 |  |  |  |  | 93.6 | 112.7 | 112.61 | 91.94 | 92.13 | 103.02 | 100.11 | 112.64 | 113.29 | 152.43 | 20 | 15 | 18 | 4 | 3 | 5 | 24 | 18 | 23 | 3 | 20 | NO |  |  |  |  | Yes | 0 | No
304449,304454,1 | 230 | 304449 EDWARDS TAP 230 304454 AURORA SS TT 230 1 | Line | Aurora SS - Greenville 230kV | 134.61 | 111.09 | 112.38 | 124.95 | 121.69 | 104.31 |  |  | 95.77 | 109.79 | 90.53 | 91.47 | 99.67 | 96.65 | 107.25 |  |  | 96.91 | 94.07 | 140.49 | 113.63 | 113.77 | 127.67 | 123.72 | 92.98 | 128.84 | 104.52 | 105.81 | 118.22 | 114.79 | 99.99 |  |  | 91.13 |  | 104.33 |  |  | 94.56 | 91.45 | 100.02 |  |  | 91.73 |  | 132.61 | 105.69 | 105.82 | 119.56 | 115.3 | 129.73 | 106.73 | 107.74 | 119.45 | 116.43 | 103.09 |  |  | 94.96 | 92.22 | 107.08 |  | 90.1 | 98.3 | 95.48 | 112.5 | 91.44 | 92.46 | 102.13 | 99.05 | 142.62 | 113.29 | 113.56 | 129.01 | 124.23 | [21 empty] | 93.96 | 93.89 |  |  |  |  | 93.93 | [19 empty] | 92.33 | 92.26 |  |  |  |  | 92.3 | [23 empty] | 96.84 | 96.77 |  |  |  |  | 96.79 | 104.31 | 142.62 | 13 | 12 | 14 | 0 | 0 | 0 | 13 | 12 | 14 | 3 | 17 | NO |  |  |  |  | Yes | 0 | No
304434,304454,1 | 230 | 304434 BAYBORO TAP 230 304454 AURORA SS TT 230 1 | Line | Aurora SS - New Bern 230kV | 145.64 | 122.4 | 123.69 | 136.35 | 133.21 | 115.9 | 99.3 | 100.21 | 107.95 | 121.11 | 103.2 | 104.1 | 111.89 | 109.16 | 118.49 | 99.52 | 100.43 | 108.61 | 105.83 | 151.72 | 125.45 | 125.59 | 139.35 | 135.56 | 105.42 | 139.88 | 116.23 | 117.19 | 129.7 | 126.42 | 111.61 | 94.62 | 95.68 | 103.42 | 100.81 | 115.99 | 98.19 | 99.2 | 107.01 | 104.2 | 111.49 | 94.93 | 95.84 | 103.73 | 101.13 | 143.84 | 117.68 | 117.81 | 131.28 | 127.2 | 140.76 | 118.36 | 119.37 | 130.9 | 127.99 | 114.66 | 98.32 | 99.21 | 107.11 | 104.62 | 118.7 | 101.81 | 102.74 | 110.54 | 107.98 | 123.69 | 103.52 | 104.5 | 113.75 | 110.82 | 153.81 | 125.08 | 125.35 | 140.63 | 136.02 | [21 empty] | 103.91 | 103.84 |  |  | 96.09 | 94.01 | 103.88 | [19 empty] | 102.31 | 102.23 |  |  | 94.15 | 91.62 | 102.27 | [9 empty] | 92.12 | 92.06 |  |  |  |  | 92.09 | [7 empty] | 106.75 | 106.68 |  |  | 98.83 | 96.46 | 106.71 | 115.9 | 153.81 | 23 | 19 | 23 | 3 | 3 | 3 | 26 | 22 | 26 | 3 | 24 | NO |  |  |  | 8538.06 | Yes | 9 | No
304022,304610,1 | 230 | 304022 BRUN1 230 TT 230 304610 SPRT &PA TAP 230 1 | Line | Brunswick Unit 1 - Delco 230kV East | 94.9 |  | 105.58 | 91.24 | 90.04 | 100.26 |  | 111.52 | 97.47 | 98.05 |  | 108.84 | 94.86 | 92.81 | 103.09 |  | 114.89 | 100.59 | 98.64 | 109.39 |  | 117.31 | 119.45 | 117.08 | 95.49 | 95.06 |  | 106.77 | 92.53 | 90.8 | 99.45 |  | 110.34 | 96.39 | 94.32 | 97.05 |  | 107.34 | 93.47 | 91.35 | 102.16 |  | 113.65 | 99.41 | 97.39 | 109.4 |  | 116.73 | 118.99 | 116.48 | 95.52 |  | 106.99 | 92.61 | 90.94 | 99.15 |  | 110.71 | 96.56 | 94.65 | 96.97 |  | 108.06 | 94.09 | 92.13 | 90.66 |  | 102.94 |  |  | 114.2 |  | 119.53 | 106.55 | 120.8 | 96.36 | 96.34 |  | 107.66 | 93.76 | 91.81 | 96.34 | 93.93 | 93.91 |  | 103.54 | 90.98 |  | 93.91 | 99.04 | 99.01 |  | 111.61 | 96.78 | 94.63 | 99.01 | 94.58 | 94.57 |  | 100.73 | 101.39 | 99.42 | 94.56 | 95.68 | 95.66 |  | 106.08 | 92.68 | 93.24 | 93.23 |  | 102.1 |  |  | 93.23 | 98.16 | 98.13 |  | 109.59 | 95.55 | 93.33 | 98.13 | 95.47 | 95.48 |  | 100.74 | 101.7 | 99.71 | 95.47 | 90.65 | 95.66 |  |  |  | 97.03 | [6 empty] | 94.35 | [6 empty] | 97.8 |  |  |  | 96.54 | 96.55 |  | 101.94 | 103.16 | 101.1 | 96.54 | 111.52 | 120.8 | 11 | 9 | 8 | 3 | 3 | 3 | 14 | 12 | 11 | 3 | 9 | YES |  |  |  | 7273.49 | Yes | 9 | Yes
304020,305004,1 | 230 | 304020 BRUN2 230 TT 230 305004 E1-PROSPECT 230 1 | Line | Brunswick Unit 2 - Whiteville 230kV | 101.16 |  |  | 91.81 | 94.32 | [14 empty] | 152.73 | 111.73 | 90.65 | 142.24 | 142.27 |  | 104.89 |  |  | 94.65 | 96.71 | [15 empty] | 156.07 | 113.93 | 93 | 144.7 | 144.46 | 109.53 |  |  | 99.07 | 101.51 | [10 empty] | 95.15 |  |  |  |  | 169.25 | 123.14 | 101.73 | 152.44 | 156.13 | [21 empty] | 113.04 | 113.18 |  |  | 106.62 | 107.34 | 113.16 | [19 empty] | 117.04 | 117.17 |  |  | 109.43 | 109.92 | 117.15 | [23 empty] | 121.41 | 121.55 |  |  | 113.95 | 114.45 | 121.52 | 0 | 169.25 | 5 | 5 | 7 | 5 | 5 | 5 | 10 | 10 | 12 | 3 | 4 | NO |  |  |  | 9204.46 | Yes | 10 | No
304052,304220,1 | 115 | 304052 CAPEFR115STT 115 304220 LILLINGTON 115 1 | Line | Cape Fear Plant - Erwin 115kV |  |  |  | 110.02 | [18 empty] | 96.16 | [5 empty] | 102.11 | [19 empty] | 100.04 | [24 empty] | 100.32 | [85 empty] | 0 | 110.02 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 2 | NO |  |  |  |  | Yes | 0 | No
304205,304218,1 | 230 | 304205 CLINTON230TT 230 304218 NEWTONGR TAP 230 1 | Line | Clinton - Erwin 230kV | 113.45 | 90.85 |  | 113.33 | 104.6 | [14 empty] | 128.01 | 101.1 | 101.24 | 124.19 | 115.8 |  | 114.45 | 90.6 |  | 112.2 | 103.83 | [15 empty] | 127.1 | 99.91 | 100.1 | 122.86 | 114.34 | 114.72 | 92 | 90.38 | 113.56 | 105.78 | [10 empty] | 100.02 |  |  | 98.65 |  | 152.65 | 116.36 | 116.87 | 145.85 | 134.51 | [84 empty] | 0 | 152.65 | 8 | 7 | 9 | 0 | 0 | 0 | 8 | 7 | 9 | 3 | 9 | NO |  |  |  | 8224.77 | Yes | 9 | No
304218,305122,1 | 230 | 304218 NEWTONGR TAP 230 305122 E15-BENSON 230 1 | Line | Clinton - Erwin 230kV | 113.61 | 90.89 |  | 113.39 | 104.63 | [14 empty] | 126.38 | 99.43 | 99.57 | 122.47 | 114.09 |  | 114.62 | 90.64 |  | 112.24 | 103.84 | [15 empty] | 125.45 | 98.23 | 98.42 | 121.13 | 112.61 | 114.89 | 92.05 | 90.42 | 113.62 | 105.81 | [10 empty] | 98.06 |  |  | 96.61 |  | 150.96 | 114.7 | 115.2 | 144.1 | 132.79 | [84 empty] | 0 | 150.96 | 6 | 6 | 8 | 0 | 0 | 0 | 6 | 6 | 8 | 3 | 9 | NO |  |  |  | 8224.77 | Yes | 9 | No
304197,305122,1 | 230 | 304197 DUNN 230 305122 E15-BENSON 230 1 | Line | Clinton - Erwin 230kV | 112.9 | 90.18 |  | 112.68 | 103.91 | [14 empty] | 125.61 | 98.67 | 98.81 | 121.69 | 113.31 |  | 113.9 |  |  | 111.53 | 103.13 | [15 empty] | 124.67 | 97.48 | 97.66 | 120.35 | 111.84 | 114.18 | 91.34 |  | 112.91 | 105.1 | [10 empty] | 97.23 |  |  | 95.79 |  | 150.17 | 113.94 | 114.45 | 143.32 | 132.02 | [84 empty] | 0 | 150.17 | 6 | 6 | 8 | 0 | 0 | 0 | 6 | 6 | 8 | 3 | 9 | NO |  |  |  |  | Yes | 0 | No
304196,304197,1 | 230 | 304196 ERWIN230 TT 230 304197 DUNN 230 1 | Line | Clinton - Erwin 230kV | 108.17 |  |  | 107.89 | 99.15 | [14 empty] | 119.85 | 92.89 | 93.03 | 115.89 | 107.57 |  | 109.05 |  |  | 106.57 | 98.25 | [15 empty] | 118.72 | 91.6 | 91.79 | 114.36 | 105.96 | 109.37 |  |  | 108.05 | 100.26 | [10 empty] | 90.58 |  |  |  |  | 144.21 | 108.1 | 108.6 | 137.31 | 126.13 | [84 empty] | 0 | 144.21 | 5 | 5 | 8 | 0 | 0 | 0 | 5 | 5 | 8 | 3 | 7 | NO |  |  |  |  | Yes | 0 | No
304266,305131,1 | 115 | 304266 FAISNHWYIND 115 305131 E15-HARGROVE 115 1 | Line | Clinton - Mount Olive 115kV | 95.52 |  |  | 90.41 | 91.35 | [14 empty] | 91.89 | [5 empty] | 95.68 |  |  |  | 90.5 | [15 empty] | 96.44 |  |  |  |  | 102.97 | 91.31 | 92.75 | 96.4 | 97.85 | [10 empty] | 103.48 | 92.26 | 92.55 | 96.93 | 97.73 | 126.19 | 105.15 | 105.28 | 115.33 | 115.4 | [84 empty] | 0 | 126.19 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 1 | 0 | NO |  |  |  | 1052.81 | Yes | 2 | No
304255,305126,1 | 115 | 304255 CLINTON115TT 115 305126 E15-CLINTON 115 1 | Line | Clinton - Vander 115kV | 97.44 |  |  | 92.06 | 90.97 | [14 empty] | 109.54 |  |  | 100.18 | 98.6 |  | 98.12 |  |  | 91.37 | 90.39 | [15 empty] | 112.9 |  |  | 103.16 | 101.29 | 104.41 |  |  | 97.33 | 97.07 | [10 empty] | 91.55 |  |  |  |  | 140.19 | 110.07 | 110.34 | 128.59 | 126.47 | [84 empty] | 0 | 140.19 | 2 | 3 | 6 | 0 | 0 | 0 | 2 | 3 | 6 | 3 | 1 | NO |  |  |  | 5151.45 | Yes | 6 | No
304515,305031,1 | 230 | 304515 WALLACE230TT 230 305031 E4-BEVERAGE 230 1 | Line | Clinton - Wallace 230kV | 110.28 |  |  | 109.26 | 102.12 | [14 empty] | 197.73 | 149.15 | 148.45 | 189.81 | 181.65 |  | 98.51 |  |  | 96.63 | [16 empty] | 193.84 | 144.62 | 142.91 | 184.63 | 176.94 | 95.25 |  |  | 94.08 | [16 empty] | 187 | 136.71 | 134.54 | 177.58 | 169.8 | [21 empty] | 159.09 | 158.98 | 113.27 | 114.01 | 153.12 | 145.11 | 158.99 | [19 empty] | 163.85 | 163.74 | 115.84 | 116.68 | 156.02 | 147.58 | 163.75 | [23 empty] | 154.6 | 154.42 | 107.52 | 108.11 | 148.32 | 140.46 | 154.43 | 0 | 197.73 | 8 | 5 | 5 | 7 | 7 | 7 | 15 | 12 | 12 | 3 | 3 | NO |  |  |  | 7860.69 | Yes | 8 | No
304205,304503,1 | 230 | 304205 CLINTON230TT 230 304503 WARSAW TAP 230 1 | Line | Clinton - Wallace 230kV | 113.88 |  |  | 111.88 | 105.1 | [14 empty] | 177.54 | 133.64 | 133.02 | 169.66 | 162.14 |  | 103.45 |  |  | 100.47 | 93.94 | [15 empty] | 174.21 | 129.59 | 128.07 | 165.18 | 157.95 | 100.59 |  |  | 98.44 | 92.11 | [15 empty] | 168.61 | 122.78 | 120.85 | 159.23 | 151.93 | [21 empty] | 115.42 | 115.34 |  |  | 110.62 | 104.41 | 115.35 | [19 empty] | 119.09 | 119.01 |  |  | 112.84 | 106.29 | 119.02 | [23 empty] | 111.96 | 111.82 |  |  | 106.92 | 100.83 | 111.83 | 0 | 177.54 | 8 | 7 | 6 | 5 | 5 | 5 | 13 | 12 | 11 | 3 | 6 | NO |  |  | 104.42 |  | Yes | 1 | No
304390,305530,1 | 230 | 304390 CUMBLND230TT 230 305530 TRNBLSOLTAP 230 1 | Line | Cumberland - Delco 230kV | 138.62 |  |  | 130.68 | 126.69 |  |  |  |  | 90.76 | [9 empty] | 182.12 | 125.04 | 121.47 | 168.34 | 162.65 |  | 136.72 |  |  | 127.22 | 122.76 | [15 empty] | 179.66 | 121.18 | 117.67 | 165.15 | 158.96 | 136.2 |  |  | 127.79 | 123.84 | [10 empty] | 97.57 |  |  |  |  | 189.83 | 128.79 | 125.26 | 173.88 | 167.68 | [21 empty] | 91.59 | 91.59 |  |  |  |  | 91.58 | [19 empty] | 95.18 | 95.18 |  |  |  |  | 95.16 | [23 empty] | 96.15 | 96.11 |  |  |  |  | 96.09 | 0 | 189.83 | 8 | 8 | 8 | 0 | 0 | 0 | 8 | 8 | 8 | 3 | 9 | NO |  |  | 132.88 |  | Yes | 1 | No
304584,305530,1 | 230 | 304584 GARLAND 230 305530 TRNBLSOLTAP 230 1 | Line | Cumberland - Delco 230kV | 129.13 |  |  | 121.52 | 117.63 | [14 empty] | 178.25 | 120.79 | 117.22 | 164.49 | 158.8 |  | 127.17 |  |  | 118.06 | 113.73 | [15 empty] | 175.75 | 116.95 | 113.43 | 161.26 | 155.09 | 126.65 |  |  | 118.61 | 114.76 | [10 empty] | 93.03 |  |  |  |  | 186.12 | 124.58 | 121.01 | 170.11 | 163.92 | [47 empty] | 90.11 | 90.12 |  |  |  |  | 90.1 | [23 empty] | 91.02 | 90.99 |  |  |  |  | 90.97 | 0 | 186.12 | 8 | 8 | 8 | 0 | 0 | 0 | 8 | 8 | 8 | 3 | 9 | NO |  |  |  | 8325.69 | Yes | 9 | No
304584,305830,1 | 230 | 304584 GARLAND 230 305830 BAYTRESOLTAP 230 1 | Line | Cumberland - Delco 230kV | 110.17 |  |  | 103.79 | 100.45 | [14 empty] | 163.56 | 111.48 | 108.23 | 151.34 | 146.26 |  | 108.33 |  |  | 100.69 | 96.98 | [15 empty] | 161.28 | 108.01 | 104.82 | 148.41 | 142.91 | 107.85 |  |  | 101.14 | 97.83 | [15 empty] | 170.76 | 114.95 | 111.67 | 156.47 | 150.94 | [21 empty] | 96.17 | 96.17 |  |  |  |  | 96.15 | [19 empty] | 99.74 | 99.74 |  |  | 90.31 |  | 99.72 | [23 empty] | 100.72 | 100.68 |  |  | 92.07 |  | 100.66 | 0 | 170.76 | 8 | 7 | 7 | 0 | 0 | 3 | 8 | 7 | 10 | 3 | 7 | NO |  |  |  |  | Yes | 0 | No
305830,900005,1 | 230 | 305830 BAYTRESOLTAP 230 900005 ID_564510 230 1 | Line | Cumberland - Delco 230kV | 97.88 |  |  | 91.95 | [15 empty] | 157.66 | 105.85 | 102.62 | 145.69 | 140.74 |  | 95.97 | [19 empty] | 155.36 | 102.43 | 99.25 | 142.73 | 137.4 | 95.49 | [19 empty] | 164.83 | 109.35 | 106.04 | 150.78 | 145.42 | [21 empty] | 96.61 | 96.61 |  |  |  |  | 96.59 | [19 empty] | 100.18 | 100.18 |  |  | 90.7 |  | 100.16 | [23 empty] | 101.15 | 101.11 |  |  | 92.46 |  | 101.08 | 0 | 164.83 | 5 | 4 | 5 | 0 | 3 | 3 | 5 | 7 | 8 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304580,305003,1 | 115 | 304580 E1WHITVLTAP 115 305003 E1-HALLSBORO 115 1 | Line | Delco - Whiteville 115kV | 110.47 |  |  | 95.5 | 102.11 | [14 empty] | 169.65 | 106.01 | 101.91 | 147.71 | 152.02 |  | 119.42 |  |  | 103.07 | 109.23 | [15 empty] | 177.13 | 111.91 | 107.91 | 154.34 | 157.96 | 107.08 |  |  | 91.18 | 98.07 | [10 empty] | 93.84 |  |  |  |  | 188.06 | 120.58 | 116.47 | 164.76 | 168.58 | [21 empty] | 102.21 | 102.45 |  |  |  | 92.09 | 102.42 | [19 empty] | 107.87 | 108.1 |  |  | 91.86 | 95.87 | 108.06 | [23 empty] | 114.61 | 114.84 |  |  | 99.33 | 103.69 | 114.8 | 0 | 188.06 | 7 | 8 | 6 | 3 | 3 | 4 | 10 | 11 | 10 | 3 | 6 | NO |  |  |  |  | Yes | 0 | No
304108,305660,1 | 115 | 304108 LOUISBURG 115 305660 FOXCRKSOLTAP 115 1 | Line | Franklinton - Spring Hope SS 115kV | 95.39 | 90.96 | 91.1 | 94.79 | 92.33 | [20 empty] | 104.44 | 98.86 | 98.98 | 102.83 | 100.01 | [20 empty] | 104.75 | 99.68 | 99.82 | 103.54 | 100.96 | [104 empty] | 0 | 104.75 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 6 | NO |  |  | 95.52 |  | Yes | 1 | No
304108,305169,1 | 115 | 304108 LOUISBURG 115 305169 LOUISBUR CAP 115 1 | Line | Franklinton - Spring Hope SS 115kV | 93.89 |  |  | 92.99 | 90.46 | [20 empty] | 102.73 | 96.75 | 96.88 | 100.74 | 97.83 | [20 empty] | 103.04 | 97.62 | 97.76 | 101.5 | 98.83 | [104 empty] | 0 | 103.04 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 4 | NO |  |  |  | 153.32 | Yes | 1 | No
304084,305172,1 | 115 | 304084 NOVOZYMES 115 305172 E18-LOUISBRG 115 1 | Line | Franklinton - Spring Hope SS 115kV | 102.18 | 96.21 | 96.34 | 100.13 | 97.26 | [20 empty] | 95.35 |  |  | 93.41 | 90.51 | [20 empty] | 95.64 | 90.3 | 90.43 | 94.14 | 91.48 | [104 empty] | 0 | 102.18 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | NO |  |  | 123.67 |  | Yes | 1 | No
304287,305052,1 | 115 | 304287 GOLDSB SSWTT 115 305052 E13-ARBA 115 1 | Line | Goldsboro SS - Kinston DuPont 115kV | 151.77 | 136.98 | 138.3 | 145.77 | 142.61 |  |  |  |  | 90.11 | [9 empty] | 105.11 | 90.64 | 90.61 | 98.63 | 95.22 |  | 148.39 | 132.82 | 134.08 | 141.37 | 137.82 | [15 empty] | 104.7 |  |  | 97.27 | 93.63 | 145.29 | 131.04 | 132.31 | 139.33 | 135.86 | [15 empty] | 93.87 | [88 empty] | 0 | 151.77 | 6 | 6 | 5 | 0 | 0 | 0 | 6 | 6 | 5 | 3 | 15 | NO |  |  |  |  | Yes | 0 | No
304510,305153,1 | 115 | 304510 WOMACKW115TT 115 305153 E17-FALL CRK 115 1 | Line | Goldsboro SS - Wommack 115kV | 120.9 | 101.64 | 103.58 | 117.12 | 113.03 | 101.54 |  |  | 96.18 | 103.44 |  |  | 97.36 | 93.73 | 93.24 |  |  |  |  | 137.55 | 116.78 | 116.8 | 130.74 | 126.82 | 92.68 | 107.52 |  | 90.24 | 103 | 98.87 | 95.23 |  |  |  |  | 96.52 |  |  | 90.17 | [6 empty] | 130.42 | 109.53 | 109.53 | 123.38 | 119.36 | 113.84 | 95.17 | 97.22 | 109.66 | 105.52 | 91.74 |  |  |  |  | 96.01 |  |  | 90.83 |  | 90.53 |  |  |  |  | 120.68 | 100.23 | 100.36 | 114.52 | 109.8 | [21 empty] | 103.41 | 103.35 |  |  | 98.42 | 95.04 | 103.36 | [19 empty] | 108.09 | 108.02 | 91.22 | 91.28 | 102.23 | 98.32 | 108.04 | [23 empty] | 92.99 | 92.93 |  |  |  |  | 92.94 | 101.54 | 137.55 | 12 | 7 | 8 | 3 | 4 | 0 | 15 | 11 | 8 | 3 | 11 | NO |  |  |  | 4379.55 | Yes | 5 | No
304509,305159,1 | 115 | 304509 PA-KIN FALL 115 305159 E17-LAGRANGE 115 1 | Line | Goldsboro SS - Wommack 115kV | 145.17 | 124.66 | 126.61 | 140.13 | 135.81 | 108.01 |  | 90.65 | 101.81 | 110.89 | 90.83 | 92.72 | 103.9 | 100.01 | 98.73 |  |  | 93.23 |  | 144.33 | 122.47 | 122.48 | 136.52 | 132.21 | 98.08 | 131.34 | 110.53 | 112.64 | 125.38 | 120.99 | 101.52 |  |  | 95.05 | 91.11 | 103.82 |  |  | 96.49 | 92.47 | 91.76 |  |  |  |  | 136.98 | 114.9 | 114.9 | 129.04 | 124.45 | 137.93 | 117.81 | 119.88 | 132.5 | 128.16 | 98.21 |  |  | 92.88 |  | 103.46 |  |  | 97.42 | 93.72 | 96.14 |  |  | 91.1 |  | 127.52 | 105.92 | 106.04 | 120.42 | 115.41 | [47 empty] | 92.42 | 92.36 |  |  |  |  | 92.37 | [30 empty] | 108.01 | 145.17 | 15 | 12 | 11 | 0 | 0 | 0 | 15 | 12 | 11 | 3 | 18 | NO |  |  |  | 4381.55 | Yes | 5 | No
304286,304288,1 | 115 | 304286 GOLDSB SSETT 115 304288 LAGRANGE 115 1 | Line | Goldsboro SS - Wommack 115kV | 145.95 | 125 | 126.96 | 140.57 | 136.12 | 102.81 |  |  | 96.34 | 106.89 |  |  | 99.61 | 95.65 | 92.3 |  |  |  |  | 139.05 | 117.06 | 117.07 | 131.11 | 126.83 | 92.54 | 132.15 | 110.84 | 112.95 | 125.78 | 121.25 | 96.36 |  |  |  |  | 99.84 |  |  | 92.19 | [6 empty] | 131.76 | 109.54 | 109.54 | 123.61 | 119.11 | 138.7 | 118.14 | 120.21 | 132.89 | 128.42 | 92.98 |  |  |  |  | 99.45 |  |  | 93.14 | [6 empty] | 122.18 | 100.5 | 100.62 | 114.94 | 109.92 | [84 empty] | 102.81 | 145.95 | 12 | 10 | 10 | 0 | 0 | 0 | 12 | 10 | 10 | 3 | 16 | NO |  |  |  |  | Yes | 0 | No
304288,305159,1 | 115 | 304288 LAGRANGE 115 305159 E17-LAGRANGE 115 1 | Line | Goldsboro SS - Wommack 115kV | 141.75 | 121.17 | 123.12 | 136.69 | 132.34 | 103.83 |  |  | 97.6 | 107.25 |  |  | 100.23 | 96.33 | 94 |  |  |  |  | 140.08 | 118.28 | 118.3 | 132.32 | 128.07 | 93.87 | 127.96 | 107.07 | 109.19 | 121.98 | 117.55 | 97.36 |  |  | 90.87 |  | 100.19 |  |  | 92.83 | [6 empty] | 132.76 | 110.76 | 110.76 | 124.83 | 120.35 | 134.52 | 114.36 | 116.42 | 129.05 | 124.68 | 94.02 |  |  |  |  | 99.81 |  |  | 93.75 | 90.04 | 91.37 |  |  |  |  | 123.23 | 101.73 | 101.86 | 116.18 | 111.2 | [84 empty] | 103.83 | 141.75 | 13 | 11 | 10 | 0 | 0 | 0 | 13 | 11 | 10 | 3 | 16 | NO |  |  |  |  | Yes | 0 | No
304509,305153,1 | 115 | 304509 PA-KIN FALL 115 305153 E17-FALL CRK 115 1 | Line | Goldsboro SS - Wommack 115kV | 119.38 | 100.14 | 102.08 | 115.61 | 111.52 | 99.95 |  |  | 94.59 | 102.03 |  |  | 95.96 | 92.33 | 91.47 |  |  |  |  | 135.9 | 115.18 | 115.2 | 129.12 | 125.22 | 91.1 | 106.04 |  |  | 101.52 | 97.39 | 93.65 |  |  |  |  | 95.13 | [9 empty] | 128.78 | 107.95 | 107.95 | 121.76 | 117.78 | 112.33 | 93.68 | 95.74 | 108.17 | 104.02 | 90.15 |  |  |  |  | 94.61 | [9 empty] | 119.04 | 98.65 | 98.78 | 112.9 | 108.2 | [21 empty] | 94 | 93.94 |  |  |  |  | 93.95 | [19 empty] | 98.35 | 98.28 |  |  | 92.91 |  | 98.29 | [30 empty] | 99.95 | 135.9 | 11 | 7 | 6 | 0 | 0 | 0 | 11 | 7 | 6 | 3 | 10 | NO |  |  |  |  | Yes | 0 | No
304484,305018,1 | 230 | 304484 HAVELOK230TT 230 305018 E2-MAYSVILLE 230 1 | Line | Grants Creek - Havelock 230kV | 100.97 | 114.23 | 111.46 | 96.55 | 97.45 | 92.12 | 105.04 | 102.28 |  | 91.57 | 103.73 | 100.99 |  |  | 93.18 | 106.4 | 103.64 | [8 empty] | 104.5 | 116.8 | 114.06 | 99.1 | 99.84 | 95.64 | 108.08 | 105.59 |  | 90.49 | 95.69 | 107.44 | 104.63 |  |  | 97.13 | 110.12 | 107.36 | 91.55 | 92.22 | [5 empty] | 106.21 | 119.14 | 116.37 | 101.43 | 102.39 | 98.59 | 111.49 | 108.73 | 93.12 | 93.82 | 97.01 | 109.14 | 106.36 | 91 | 91.8 |  | 102.15 | 99.36 | [7 empty] | 91.57 | 91.67 | 106.28 | 103.14 |  |  | 91.64 | 91.1 | 91.19 | 104.33 | 101.19 |  |  | 91.16 | 97.3 | 97.39 | 112.24 | 109.13 | 92.13 | 93.08 | 97.36 | [7 empty] | 93.34 | 93.43 | 107.19 | 103.97 |  | 93.14 | 93.22 | 105.11 | 102.14 |  |  | 93.2 | 100.07 | 100.16 | 114.47 | 111.23 | 94.35 | 95.09 | 100.13 | [8 empty] | 93.4 |  |  | 103.41 | 100.27 | [5 empty] | 99.79 | 96.67 | [5 empty] | 101.22 | 98.1 | [10 empty] | 111.49 | 119.14 | 9 | 9 | 10 | 2 | 5 | 1 | 11 | 14 | 11 | 3 | 23 | YES |  |  |  | 5091.85 | Yes | 7 | No
304527,305018,1 | 230 | 304527 SWANSBORO 230 305018 E2-MAYSVILLE 230 1 | Line | Grants Creek - Havelock 230kV | 94.38 | 107.62 | 104.87 |  | 90.85 |  | 98.01 | 95.24 |  |  | 97.49 | 94.74 |  |  |  | 98.58 | 95.82 | [8 empty] | 97.92 | 110.19 | 107.44 | 92.5 | 93.24 |  | 101.05 | 98.57 |  |  |  | 101.24 | 98.37 |  |  |  | 102.31 | 99.54 | [7 empty] | 99.6 | 112.53 | 109.76 | 94.84 | 95.8 | 91.54 | 104.47 | 101.71 |  |  | 90.78 | 102.89 | 100.1 |  |  |  | 94.35 | 91.52 | [9 empty] | 91.33 | [6 empty] | 90.38 | [6 empty] | 95.79 | 92.83 | [12 empty] | 92.18 |  |  |  |  | 91.08 | [6 empty] | 97.89 | 94.86 | [40 empty] | 104.47 | 112.53 | 2 | 5 | 6 | 0 | 0 | 0 | 2 | 5 | 6 | 3 | 9 | NO |  |  |  |  | Yes | 0 | No
304518,304527,1 | 230 | 304518 GRNTSCK230TT 230 304527 SWANSBORO 230 1 | Line | Grants Creek - Havelock 230kV | 94.3 | 107.43 | 104.67 |  | 90.63 |  | 95.92 | 93.15 |  |  | 95.81 | 93.06 |  |  |  | 96.08 | 93.31 | [8 empty] | 97.85 | 109.97 | 107.22 | 92.3 | 93 |  | 98.95 | 96.47 |  |  |  | 99.56 | 96.66 |  |  |  | 99.81 | 97.03 | [7 empty] | 99.52 | 112.33 | 109.56 | 94.66 | 95.58 |  | 102.39 | 99.63 |  |  |  | 101.21 | 98.41 |  |  |  | 91.86 | [92 empty] | 102.39 | 112.33 | 2 | 2 | 4 | 0 | 0 | 0 | 2 | 2 | 4 | 3 | 7 | NO |  |  |  |  | Yes | 0 | No
304451,304452,1 | 230 | 304451 GREENVILE TT 230 304452 GREENVILE W 230 1 | Line | Greenville - Wilson 230kV | 101.56 |  |  | 91.63 | [15 empty] | 102.79 |  |  | 90.34 |  |  | 95.38 | [19 empty] | 94.07 |  |  |  |  | 96.26 | [19 empty] | 106.88 |  |  | 93.68 | [85 empty] | 0 | 106.88 | 2 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 1 | NO |  |  |  | 8001.33 | Yes | 9 | No
304229,304289,1 | 230 | 304229 PA-FARMVILLE 230 304289 FARMVILLE 230 1 | Line | Greenville - Wilson 230kV | 103.24 |  |  | 93.62 | [15 empty] | 93.23 | [5 empty] | 96.98 | [24 empty] | 99.37 | [19 empty] | 97.66 | [88 empty] | 0 | 103.24 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304466,304467,1 | 115 | 304466 NEWBER115NTT 115 304467 AMITAL TAP 115 1 | Line | Havelock - New Bern 115kV | 108.54 | 121.48 | 119.15 | 106.21 | 107.53 | 107.35 | 119.96 | 117.72 | 104.39 | 99.53 | 111.54 | 109.29 | 96.29 | 97.41 | 116.42 | 129.01 | 126.58 | 113.6 | 114.72 | [5 empty] | 105.57 | 111.46 | 123.78 | 121.57 | 108.56 | 109.83 | 110.49 | 122.75 | 120.5 | 107.23 | 108.29 | 103.07 | 114.73 | 112.45 | 99.51 | 100.54 | 119.78 | 131.94 | 129.75 | 116.69 | 117.7 | [5 empty] | 113.71 | 126.23 | 123.97 | 111.06 | 112.43 | 113.53 | 126.12 | 123.91 | 110.46 | 111.71 | 104.53 | 116.67 | 114.41 | 101.33 | 102.53 | 113.7 | 126.09 | 123.94 | 111.15 | 112.36 | [5 empty] | 91.37 | 91.43 | 102.51 | 100.54 |  | 90.18 | 91.41 |  |  | 95.06 | 93.03 |  |  |  | 102.15 | 102.21 | 113.28 | 111.26 | 99.8 | 100.84 | 102.2 | [7 empty] | 92.31 | 92.37 | 103.06 | 100.97 |  |  |  | 95.66 | 93.63 |  |  |  | 103.62 | 103.69 | 114.49 | 112.45 | 101.02 | 101.97 | 103.67 | [7 empty] | 90.8 | 92.35 |  |  | 100.72 | 98.68 | [5 empty] | 92.28 | 90.25 |  |  |  | 94.72 | 94.78 | 106.18 | 104.1 | 92.89 | 94.01 | 94.76 | [7 empty] | 126.12 | 131.94 | 17 | 19 | 20 | 6 | 7 | 2 | 23 | 26 | 22 | 3 | 34 | YES |  |  |  | 3150.04 | Yes | 5 | No
304460,304485,1 | 115 | 304460 PA-NBLFRDTAP 115 304485 HAVLOK115NTT 115 1 | Line | Havelock - New Bern 115kV | 90.45 | 102.24 | 100.13 |  |  |  | 100.49 | 98.44 |  |  | 93.67 | 91.62 |  |  | 96.27 | 107.89 | 106.12 | 93.7 | 94.74 | [6 empty] | 93.11 | 104.36 | 102.32 | 90.1 | 91.28 | 91.8 | 103 | 100.94 |  |  |  | 96.54 | 94.5 |  |  | 99.37 | 110.59 | 108.56 | 96.5 | 97.46 | [5 empty] | 95.13 | 106.61 | 104.53 | 92.39 | 93.64 | 94.57 | 106.08 | 104.05 | 91.78 | 92.92 |  | 98.31 | 96.24 |  |  | 93.75 | 105.59 | 103.21 | 91.42 | 92.55 | [7 empty] | 93.69 | 91.71 | [10 empty] | 92.52 | 92.58 | 104.04 | 102.03 | 90.19 | 91.23 | 92.56 | [9 empty] | 94.25 | 92.18 | [8 empty] | 94.03 | 94.09 | 104.87 | 102.83 | 91.46 | 92.4 | 94.07 | [11 empty] | 91.93 | [13 empty] | 96.51 | 94.45 | [10 empty] | 106.08 | 110.59 | 5 | 6 | 6 | 2 | 2 | 0 | 7 | 8 | 6 | 3 | 11 | YES |  |  |  | 2805.04 | Yes | 4 | No
304460,304467,1 | 115 | 304460 PA-NBLFRDTAP 115 304467 AMITAL TAP 115 1 | Line | Havelock - New Bern 115kV | 96.28 | 108.14 | 106.01 | 94 | 95.21 | 95.17 | 106.74 | 104.69 | 92.46 |  | 99.09 | 97.03 |  |  | 103.4 | 115 | 112.92 | 100.81 | 101.85 | [5 empty] | 93.54 | 98.96 | 110.25 | 108.22 | 96.16 | 97.33 | 98.04 | 109.29 | 107.22 | 95.05 | 96.02 | 91.16 | 102 | 99.93 |  |  | 106.49 | 117.7 | 115.68 | 103.64 | 104.58 | [5 empty] | 101.01 | 112.51 | 110.43 | 98.46 | 99.72 | 100.82 | 112.38 | 110.34 | 98.01 | 99.16 | 92.49 | 103.77 | 101.7 |  | 90.66 | 100.89 | 112.44 | 110.33 | 98.55 | 99.67 | [7 empty] | 99 | 97.03 | [5 empty] | 91.69 |  |  |  |  | 98.56 | 98.62 | 109.8 | 107.79 | 96.22 | 97.26 | 98.61 | [9 empty] | 99.55 | 97.47 |  |  |  | 92.3 | 90.28 |  |  |  | 100.04 | 100.1 | 110.88 | 108.85 | 97.46 | 98.4 | 100.09 | [11 empty] | 97.23 | 95.2 | [10 empty] | 91.19 | 91.25 | 102.57 | 100.5 |  | 90.48 | 91.23 | [7 empty] | 112.38 | 117.7 | 9 | 10 | 11 | 2 | 5 | 2 | 11 | 15 | 13 | 3 | 14 | YES |  |  |  |  | Yes | 1 | No
304465,304484,1 | 230 | 304465 NEWBERN230TT 230 304484 HAVELOK230TT 230 1 | Line | Havelock - New Bern 230kV | 155.86 | 169.07 | 166.17 | 151.07 | 151.91 | 149.47 | 162.32 | 159.46 | 143.31 | 143.23 | 155.24 | 152.41 | 136.56 | 137.13 | 156.24 | 169.45 | 166.57 | 150.25 | 151.03 | 100.03 | 113.08 | 112.94 | 96.62 | 98.04 | 144.03 | 159.51 | 171.72 | 168.87 | 153.66 | 154.33 | 152.97 | 165.31 | 162.85 | 146.72 | 147.31 | 147.35 | 158.88 | 156.04 | 140.41 | 140.88 | 160.12 | 173.3 | 170.42 | 154.2 | 154.79 | 104.39 | 116.83 | 117.03 | 100.6 | 101.78 | 161.21 | 174.18 | 171.31 | 156.1 | 157 | 156.03 | 168.89 | 166.01 | 150.16 | 150.67 | 148.81 | 160.75 | 157.88 | 142.28 | 143 | 151.76 | 165 | 162.15 | 146.36 | 147.22 | 111.8 | 123.61 | 123.37 | 107.06 | 108.35 | 151.16 | 151.26 | 166.15 | 162.9 | 145.45 | 146.26 | 151.23 | 144.9 | 145 | 158.05 | 154.79 | 138.26 | 138.91 | 144.97 | 163.38 | 163.48 | 178.33 | 175.07 | 157.92 | 158.81 | 163.45 | 102.99 | 103.09 | 117.09 | 116.58 | 99.3 | 100.88 | 103.06 | 152.98 | 153.07 | 167.03 | 163.88 | 146.53 | 147 | 147.09 | 158.71 | 155.7 | 139.45 | 139.81 | 147.07 | 166.24 | 166.33 | 180.91 | 177.49 | 160.14 | 160.78 | 166.3 | 104.87 | 104.97 | 118.51 | 118 | 100.91 | 102.66 | 104.94 | 147.13 | 153.04 | 148.71 | 148.81 | 163.34 | 160.05 | 143 | 143.99 | 148.78 | 140.13 | 140.23 | 153.37 | 150.13 | 134.23 | 135.09 | 140.2 | 152.05 | 152.15 | 167.12 | 163.83 | 146.82 | 147.96 | 152.12 | 109.9 | 109.99 | 123.36 | 122.57 | 105.97 | 107.35 | 109.96 | 168.89 | 180.91 | 23 | 25 | 25 | 13 | 16 | 14 | 36 | 41 | 39 | 3 | 50 | YES |  |  |  | 5158.29 | Yes | 7 | No
304528,305540,1 | 230 | 304528 RHEMS 230 305540 TRENTRSOLTAP 230 1 | Line | Jacksonville - New Bern 230kV |  | 105.7 | 102.4 |  |  | 99.18 | 117.24 | 113.93 | 94.81 | 94.53 | 111.77 | 108.63 |  | 91.35 | 105.08 | 123.63 | 120.18 | 100.75 | 102.46 | [5 empty] | 96.53 | 95.12 | 113.5 | 110.16 | 91.18 | 93.19 | 103.36 | 120.92 | 117.59 | 98.59 | 100.14 | 99.33 | 116.17 | 112.95 | 94.11 | 95.63 | 109.73 | 127.91 | 124.57 | 105.14 | 106.7 | [5 empty] | 108.42 | 126.7 | 123.31 | 104.29 | 106.32 | 114.89 | 132.76 | 129.41 | 110 | 111.73 | 108.4 | 125.62 | 122.28 | 103.31 | 104.98 | 107.85 | 125.92 | 122.6 | 103.64 | 105.42 | [5 empty] | 104.34 | 104.44 | 121.21 | 117.94 | 99.97 | 101.39 | 104.41 | 99.75 | 99.84 | 115.71 | 112.4 | 94.96 | 96.29 | 99.82 | 115.14 | 115.24 | 132 | 128.76 | 110.7 | 112.14 | 115.21 | [7 empty] | 102.03 | 102.12 | 118.32 | 115.04 | 97.36 | 97.83 | 97.84 | 113.05 | 109.74 | 92.63 | 93.81 | 97.82 | 113.81 | 113.91 | 130.58 | 127.22 | 109.12 | 110.44 | 113.88 | [7 empty] | 98.69 | 102.1 | 101.95 | 102.05 | 118.5 | 115.19 | 97.77 | 99.36 | 102.02 | 95.23 | 95.32 | 111.1 | 107.69 | 90.77 | 92.27 | 95.3 | 103.38 | 103.48 | 120.73 | 117.41 | 99.53 | 101.23 | 103.45 | [7 empty] | 132.76 | 132.76 | 11 | 13 | 20 | 7 | 8 | 6 | 18 | 21 | 26 | 3 | 36 | NO |  |  |  | 4866.27 | Yes | 5 | No
304471,304528,1 | 230 | 304471 CC WD EN TAP 230 304528 RHEMS 230 1 | Line | Jacksonville - New Bern 230kV |  | 104.98 | 101.69 |  |  | 100.31 | 118.49 | 115.18 | 96.03 | 95.32 | 112.67 | 109.53 | 90.6 | 92.26 | 106.56 | 125.21 | 121.76 | 102.31 | 104.05 | [5 empty] | 97.78 | 94.28 | 112.81 | 109.47 | 90.48 | 92.52 | 104.51 | 122.18 | 118.85 | 99.82 | 101.41 | 100.13 | 117.09 | 113.87 | 95.01 | 96.56 | 111.21 | 129.51 | 126.16 | 106.7 | 108.29 | [5 empty] | 107.58 | 125.99 | 122.6 | 103.57 | 105.64 | 116.04 | 134.02 | 130.66 | 111.23 | 112.99 | 109.21 | 126.53 | 123.2 | 104.21 | 105.9 | 109.35 | 127.51 | 124.19 | 105.21 | 107.02 | [5 empty] | 107.64 | 107.74 | 124.52 | 121.26 | 103.27 | 104.69 | 107.72 | 102.67 | 102.76 | 118.65 | 115.34 | 97.89 | 99.21 | 102.74 | 118.83 | 118.93 | 135.7 | 132.45 | 114.39 | 115.83 | 118.9 | [7 empty] | 105.33 | 105.42 | 121.63 | 118.35 | 100.65 | 100.75 | 100.76 | 115.99 | 112.67 | 95.55 | 96.73 | 100.74 | 117.5 | 117.6 | 134.28 | 130.91 | 112.8 | 114.13 | 117.57 | [7 empty] | 101.99 | 105.4 | 105.25 | 105.35 | 121.81 | 118.5 | 101.07 | 102.66 | 105.32 | 98.15 | 98.24 | 114.03 | 110.62 | 93.69 | 95.19 | 98.22 | 107.06 | 107.16 | 124.42 | 121.1 | 103.21 | 104.9 | 107.13 | [7 empty] | 134.02 | 135.7 | 12 | 14 | 20 | 7 | 9 | 7 | 19 | 23 | 27 | 3 | 42 | YES |  |  |  | 4866.27 | Yes | 6 | No
304465,304471,1 | 230 | 304465 NEWBERN230TT 230 304471 CC WD EN TAP 230 1 | Line | Jacksonville - New Bern 230kV |  | 98.02 | 94.73 |  |  | 93.07 | 111.66 | 108.35 |  |  | 105.87 | 102.73 |  |  | 99.32 | 118.35 | 114.9 | 95.42 | 97.25 | [5 empty] | 91.02 |  | 105.9 | 102.56 |  |  | 97.26 | 115.39 | 112.06 | 93 | 94.69 | 92.89 | 110.34 | 107.12 |  |  | 103.97 | 122.68 | 119.33 | 99.84 | 101.53 | [5 empty] | 100.38 | 119.07 | 115.68 | 96.62 | 98.76 | 108.82 | 127.18 | 123.83 | 104.36 | 106.22 | 101.97 | 119.72 | 116.39 | 97.36 | 99.16 | 102.13 | 120.64 | 117.32 | 98.32 | 100.22 | [5 empty] | 103.16 | 103.27 | 120.69 | 117.38 | 99.04 | 100.58 | 103.24 | 98.11 | 98.2 | 114.74 | 111.38 | 93.6 | 95.05 | 98.18 | 114.57 | 114.67 | 132.03 | 128.73 | 110.34 | 111.9 | 114.64 | [7 empty] | 100.8 | 100.9 | 117.78 | 114.45 | 96.42 | 96.15 | 96.16 | 112.09 | 108.73 | 91.26 | 92.59 | 96.13 | 113.2 | 113.3 | 130.63 | 127.22 | 108.75 | 110.2 | 113.27 | [7 empty] | 97.88 | 100.87 | 100.74 | 100.83 | 117.9 | 114.55 | 96.78 | 98.49 | 100.81 | 93.51 | 93.61 | 110.02 | 106.56 |  | 90.94 | 93.59 | 102.58 | 102.68 | 120.56 | 117.19 | 98.94 | 100.75 | 102.65 | [7 empty] | 127.18 | 132.03 | 6 | 10 | 15 | 7 | 8 | 6 | 13 | 18 | 21 | 3 | 30 | YES |  |  |  | 4866.27 | Yes | 6 | No
305076,305077,1 | 230 | 305076 E9-HORACE 230 305077 E9-RAMSEY RD 230 1 | Line | Jacksonville - New Bern 230kV | 158.17 | 175.08 | 171.7 | 152.71 | 154.15 | 134.47 | 150.98 | 147.63 | 128.26 | 129.7 | 145.01 | 141.64 | 122.89 | 123.99 | 140.3 | 157.6 | 153.9 | 134.87 | 136.12 |  | 92.82 | 92.68 |  |  | 129.5 | 157.51 | 173.2 | 169.81 | 150.58 | 151.82 | 138.93 | 154.7 | 151.36 | 132.14 | 133.14 | 134.75 | 149.32 | 145.98 | 127.29 | 128.22 | 145.13 | 161.69 | 158.37 | 138.68 | 139.72 |  | 97.11 | 97.27 |  |  | 149.45 | 166.27 | 162.86 | 143.7 | 145.35 | 135.1 | 152.04 | 148.69 | 129.21 | 130.68 | 128.39 | 144.75 | 141.38 | 122.4 | 123.79 | 128.23 | 145.21 | 141.82 | 123.07 | 124.59 |  | 98.22 | 97.97 |  |  | 103.58 | 103.68 | 120.43 | 117.18 | 99.22 | 100.64 | 103.65 | 99.11 | 99.2 | 115.03 | 111.73 | 94.35 | 95.66 | 99.18 | 114.31 | 114.41 | 131.08 | 127.84 | 109.87 | 111.31 | 114.38 | [7 empty] | 109.36 | 109.45 | 125.13 | 121.86 | 104.28 | 105.29 | 105.29 | 119.93 | 116.61 | 99.62 | 100.67 | 105.27 | 121.12 | 121.22 | 137.41 | 134.05 | 116.02 | 117.22 | 121.19 | [7 empty] | 105.48 | 109.43 | 101.2 | 101.29 | 117.7 | 114.41 | 97.03 | 98.61 | 101.27 | 94.61 | 94.7 | 110.42 | 107.03 | 90.17 | 91.67 | 94.68 | 102.54 | 102.64 | 119.89 | 116.57 | 98.7 | 100.38 | 102.61 | [7 empty] | 154.7 | 175.08 | 20 | 20 | 20 | 7 | 9 | 6 | 27 | 29 | 26 | 3 | 47 | YES |  |  |  | 5921.44 | Yes | 7 | No
304524,305077,1 | 230 | 304524 JACKSON230TT 230 305077 E9-RAMSEY RD 230 1 | Line | Jacksonville - New Bern 230kV | 156.06 | 172.97 | 169.59 | 150.58 | 152.01 | 132.21 | 148.72 | 145.37 | 126 | 127.7 | 143.02 | 139.67 | 120.88 | 121.99 | 137.79 | 155.09 | 151.4 | 132.33 | 133.58 |  | 90.51 | 90.36 |  |  | 127.24 | 155.38 | 171.09 | 167.69 | 148.46 | 149.7 | 136.66 | 152.44 | 149.1 | 129.87 | 130.87 | 132.75 | 147.34 | 143.99 | 125.29 | 126.21 | 142.62 | 159.19 | 155.86 | 136.17 | 137.21 |  | 94.81 | 94.96 |  |  | 147.34 | 164.16 | 160.75 | 141.59 | 143.25 | 132.86 | 149.8 | 146.45 | 126.96 | 128.44 | 126.42 | 142.77 | 139.4 | 120.42 | 121.81 | 125.69 | 142.71 | 139.33 | 120.53 | 122.06 |  | 95.96 | 95.7 |  |  | 100.97 | 101.07 | 117.84 | 114.58 | 96.61 | 98.03 | 101.05 | 96.79 | 96.88 | 112.73 | 109.43 | 92.02 | 93.33 | 96.86 | 111.39 | 111.48 | 128.24 | 124.99 | 106.95 | 108.39 | 111.46 | [7 empty] | 106.75 | 106.84 | 122.55 | 119.27 | 101.66 | 102.97 | 102.97 | 117.63 | 114.31 | 97.29 | 98.34 | 102.95 | 118.21 | 118.31 | 134.53 | 131.17 | 113.11 | 114.31 | 118.28 | [7 empty] | 102.86 | 106.82 | 98.59 | 98.69 | 115.12 | 111.82 | 94.41 | 96 | 98.66 | 92.28 | 92.37 | 108.12 | 104.72 |  |  | 92.35 | 99.63 | 99.73 | 116.97 | 113.65 | 95.78 | 97.47 | 99.7 | [7 empty] | 152.44 | 172.97 | 20 | 20 | 20 | 7 | 9 | 2 | 27 | 29 | 22 | 3 | 43 | YES |  |  |  |  | Yes | 1 | No
305076,305540,1 | 230 | 305076 E9-HORACE 230 305540 TRENTRSOLTAP 230 1 | Line | Jacksonville - New Bern 230kV | 100.7 | 119.11 | 115.8 | 96.87 | 98.82 | 106.03 | 123.81 | 120.49 | 101.3 | 101.35 | 118.24 | 115.06 | 96.13 | 97.67 | 111.96 | 130.27 | 126.78 | 107.36 | 108.99 | [5 empty] | 102.94 | 108.95 | 126.83 | 123.48 | 104.45 | 106.31 | 110.26 | 127.49 | 124.15 | 105.09 | 106.54 | 106.19 | 122.62 | 119.38 | 100.53 | 101.94 | 116.63 | 134.53 | 131.18 | 111.68 | 113.14 | [5 empty] | 122.39 | 140.21 | 136.81 | 117.73 | 119.64 | 121.94 | 139.52 | 136.16 | 116.71 | 118.36 | 115.36 | 132.29 | 128.94 | 109.95 | 111.52 | 114.96 | 132.71 | 129.36 | 110.42 | 112.12 | [5 empty] | 104.5 | 104.6 | 121.35 | 118.11 | 100.14 | 101.56 | 104.57 | 99.92 | 100.01 | 115.84 | 112.54 | 95.16 | 96.47 | 99.99 | 115.35 | 115.44 | 132.1 | 128.87 | 110.91 | 112.35 | 115.41 | [7 empty] | 102.17 | 102.26 | 118.42 | 115.15 | 97.51 | 97.98 | 97.99 | 113.17 | 109.86 | 92.79 | 93.97 | 97.97 | 113.98 | 114.07 | 130.7 | 127.35 | 109.28 | 110.6 | 114.05 | [7 empty] | 98.84 | 102.23 | 102.12 | 102.22 | 118.62 | 115.32 | 97.95 | 99.53 | 102.19 | 95.42 | 95.51 | 111.24 | 107.84 | 90.98 | 92.48 | 95.49 | 103.57 | 103.67 | 120.92 | 117.61 | 99.72 | 101.41 | 103.64 | [7 empty] | 139.52 | 140.21 | 16 | 20 | 20 | 7 | 8 | 6 | 23 | 28 | 26 | 3 | 44 | NO |  |  |  |  | Yes | 0 | No
304477,304480,1 | 115 | 304477 VOA TAP 115 304480 KINSDUP115TT 115 1 | Line | Kinston DuPont - New Bern 115kV | 214.6 | 190.26 | 192.14 | 205.67 | 201.13 | 180.63 | 154.67 | 156.49 | 168.95 | 186.57 | 159.55 | 161.35 | 173.81 | 168.56 | 174.08 | 148.83 | 150.63 | 163.21 | 158.5 | 228.75 | 191.31 | 191.31 | 211.39 | 204.65 | 164.01 | 212.3 | 186.4 | 188.28 | 201.71 | 196.69 | 177.72 | 150.87 | 152.85 | 165.34 | 160.15 | 183.19 | 154.97 | 156.96 | 169.39 | 163.91 | 170.73 | 145.04 | 146.85 | 159.42 | 154.45 | 219.28 | 187.4 | 187.45 | 202.09 | 196.05 | 211.23 | 186.58 | 188.56 | 201.88 | 197.11 | 175.76 | 150.55 | 152.35 | 164.95 | 160.14 | 182.7 | 156.61 | 158.46 | 170.87 | 165.84 | 177 | 152.21 | 154.12 | 166.82 | 161.96 | 221.42 | 182.99 | 183.1 | 204.26 | 196.65 | 116.53 | 116.48 | 97.44 | 98.82 | 108.79 | 105.09 | 116.49 | 121.19 | 121.14 | 101.25 | 102.58 | 112.59 | 108.65 | 121.15 | 112.06 | 111.97 | 90.46 | 91.86 | 103.59 | 100.21 | 112.02 | 150.83 | 150.74 | 126.03 | 126.25 | 140.46 | 136.54 | 150.78 | 115.45 | 115.4 | 95.34 | 96.9 | 106.67 | 119.98 | 119.93 | 98.68 | 100.06 | 110.06 | 105.79 | 119.94 | 110.49 | 110.4 |  |  | 101.35 | 97.63 | 110.44 | 150.23 | 150.13 | 124.11 | 124.3 | 139.02 | 134.48 | 150.17 | 102.65 | 115.42 | 119.69 | 119.6 | 99.13 | 100.49 | 110.76 | 107.19 | 119.64 | 126.83 | 126.74 | 103.97 | 105.33 | 116.93 | 113.11 | 126.78 | 120.93 | 120.83 | 97.17 | 98.93 | 112.26 | 108.69 | 120.88 | 149.45 | 149.35 | 124.19 | 124.39 | 139.16 | 135.06 | 149.38 | 180.63 | 228.75 | 25 | 25 | 25 | 12 | 13 | 12 | 37 | 38 | 37 | 3 | 45 | NO |  |  |  | 6789.59 | Yes | 7 | No
304475,304477,1 | 115 | 304475 WEYER TAP 115 304477 VOA TAP 115 1 | Line | Kinston DuPont - New Bern 115kV | 155.97 | 135.02 | 136.83 | 149.27 | 145.63 | 154.07 | 130.18 | 131.98 | 144.06 | 160.02 | 135.28 | 137.06 | 149.11 | 144.43 | 147.24 | 123.96 | 125.75 | 137.98 | 133.76 | 199.67 | 165.96 | 165.97 | 184.54 | 178.12 | 139.64 | 153.56 | 131.3 | 133.12 | 145.64 | 141.63 | 151.19 | 126.38 | 128.4 | 140.51 | 135.9 | 156.71 | 130.77 | 132.74 | 144.9 | 140 | 143.89 | 120.29 | 122.08 | 134.26 | 129.88 | 190.55 | 162.1 | 162.18 | 176.03 | 170.69 | 152.52 | 131.4 | 133.3 | 145.61 | 141.77 | 149.15 | 125.93 | 127.7 | 140 | 135.64 | 156.2 | 132.25 | 134.06 | 146.12 | 141.63 | 149.9 | 127.1 | 129 | 141.21 | 136.93 | 192.07 | 157.79 | 157.9 | 177.11 | 170.34 | 117.97 | 117.92 | 98.87 | 100.26 | 110.22 | 106.52 | 117.93 | 122.63 | 122.58 | 102.68 | 104.01 | 114.03 | 110.09 | 122.59 | 113.54 | 113.45 | 91.89 | 93.3 | 105.07 | 101.69 | 113.49 | 152.35 | 152.25 | 127.52 | 127.74 | 141.96 | 138.03 | 152.29 | 116.89 | 116.84 | 96.77 | 98.33 | 108.1 | 121.42 | 121.37 | 100.11 | 101.48 | 111.49 | 107.22 | 121.39 | 111.96 | 111.87 |  | 90.99 | 102.83 | 99.1 | 111.91 | 151.74 | 151.64 | 125.59 | 125.78 | 140.5 | 135.96 | 151.68 | 104.08 | 116.85 | 121.17 | 121.07 | 100.56 | 101.92 | 112.24 | 108.66 | 121.11 | 128.32 | 128.23 | 105.4 | 106.77 | 118.4 | 114.58 | 128.27 | 122.43 | 122.33 | 98.63 | 100.39 | 113.74 | 110.17 | 122.37 | 150.97 | 150.87 | 125.66 | 125.87 | 140.67 | 136.56 | 150.9 | 154.07 | 199.67 | 25 | 25 | 25 | 12 | 13 | 13 | 37 | 38 | 38 | 3 | 47 | NO |  |  |  | 6709.59 | Yes | 7 | No
304466,304475,1 | 115 | 304466 NEWBER115NTT 115 304475 WEYER TAP 115 1 | Line | Kinston DuPont - New Bern 115kV | 152.05 | 131.59 | 133.46 | 146.19 | 142.67 | 149.69 | 126.9 | 128.74 | 140.93 | 155.69 | 132.16 | 133.98 | 146.13 | 141.78 | 142.91 | 120.61 | 122.44 | 134.78 | 130.83 | 196.62 | 163.08 | 163.09 | 182.29 | 176.19 | 136.81 | 149.67 | 128.14 | 130.01 | 142.73 | 138.89 | 146.79 | 123.28 | 125.3 | 137.51 | 133.22 | 152.33 | 127.83 | 129.84 | 142.02 | 137.5 | 139.56 | 117.03 | 118.86 | 131.15 | 127.04 | 187.32 | 159.32 | 159.39 | 173.52 | 168.38 | 148.62 | 128.05 | 130.01 | 142.57 | 138.88 | 144.76 | 122.55 | 124.36 | 136.73 | 132.68 | 151.82 | 128.99 | 130.85 | 142.99 | 138.8 | 145.71 | 123.78 | 125.72 | 138.09 | 134.02 | 189.1 | 154.75 | 154.86 | 174.9 | 168.22 | 111.81 | 111.76 | 94.22 | 95.6 | 105.21 | 101.9 | 111.78 | 116.31 | 116.26 | 97.98 | 99.31 | 108.96 | 105.44 | 116.27 | 108.05 | 107.96 |  |  | 100.85 | 97.85 | 108 | 145.72 | 145.63 | 122.5 | 122.73 | 136.36 | 132.78 | 145.67 | 110.7 | 110.65 | 92.28 | 93.84 | 103.23 | 115.08 | 115.04 | 95.64 | 97 | 106.62 | 102.83 | 115.05 | 106.47 | 106.38 |  |  | 98.78 | 95.45 | 106.42 | 145.1 | 145.01 | 120.67 | 120.88 | 135.03 | 130.86 | 145.04 | 99.67 | 110.67 | 115.35 | 115.26 | 95.88 | 97.23 | 107.69 | 104.49 | 115.29 | 122.4 | 122.31 | 100.63 | 101.99 | 113.65 | 110.24 | 122.34 | 116.73 | 116.63 | 94.47 | 96.19 | 109.08 | 105.85 | 116.68 | 144.47 | 144.38 | 120.57 | 120.79 | 135.18 | 131.41 | 144.41 | 149.69 | 196.62 | 25 | 25 | 25 | 11 | 11 | 12 | 36 | 36 | 37 | 3 | 43 | NO |  |  |  | 6709.59 | Yes | 7 | No
304192,304251,1 | 230 | 304192 SELMA 230 TT 230 304251 LEESUB230 TT 230 1 | Line | Lee - Selma 230kV | 128.41 | 102.34 | 102.89 | 123.44 | 114.9 | 93.52 |  |  |  | 112.3 |  |  | 104.93 | 96.3 | 108.65 |  |  | 103.03 | 94.37 | 136.63 | 103.23 | 103.67 | 127.38 | 117.97 |  | 126.95 | 98.97 | 99.58 | 120 | 111.22 | [5 empty] | 104.77 |  |  | 97.52 |  | 102.77 |  |  | 97.52 |  | 130.67 | 96.76 | 97.2 | 121.25 | 111.4 | 130.49 | 102.83 | 103.4 | 123.54 | 115.69 | 105.44 |  |  | 99.72 | 91.73 | 113.56 |  |  | 106.54 | 98.5 | 131.13 | 104.12 | 104.71 | 124.5 | 115.65 | 170.67 | 131.7 | 132.31 | 158.32 | 148.02 | [47 empty] | 93.31 | 93.22 |  |  |  |  | 93.19 |  |  | 93.64 | 93.48 |  |  |  |  | 93.48 | 106.94 | 106.78 |  |  | 99.81 | 91.63 | 106.78 | 103.07 | 102.91 |  |  | 97.85 |  | 102.9 | 117.31 | 117.22 |  |  | 109.64 | 101.13 | 117.16 | 105.44 | 170.67 | 14 | 8 | 18 | 0 | 0 | 8 | 14 | 8 | 26 | 3 | 14 | NO |  |  |  |  | Yes | 0 | No
304267,304500,1 | 230 | 304267 GRANTHAM 230 304500 WOMMACK230TT 230 1 | Line | Lee - Wommack 230kV North | 151.87 | 138.5 | 140.14 | 148.96 | 145.61 | 101.22 |  |  | 96.94 | 105.2 | 90.1 | 91.73 | 100.48 | 96.72 | [5 empty] | 125.75 | 112.72 | 112.62 | 121.79 | 118.09 | 93.3 | 140.33 | 126.14 | 127.89 | 136.35 | 132.75 | 99.04 |  |  | 94.11 | 90.32 | 102.59 |  |  | 97 | 93.03 | [5 empty] | 123.05 | 109.58 | 109.47 | 118.43 | 114.67 | 143.6 | 129.83 | 131.54 | 140.47 | 136.81 | 93.05 |  |  |  |  | 99.38 |  |  | 95.54 | 91.83 | [5 empty] | 110.63 | 98.72 | 98.68 | 107.4 | 103.79 | [84 empty] | 101.22 | 151.87 | 13 | 11 | 8 | 0 | 0 | 0 | 13 | 11 | 8 | 3 | 16 | NO |  |  |  |  | Yes | 0 | No
304251,304267,1 | 230 | 304251 LEESUB230 TT 230 304267 GRANTHAM 230 1 | Line | Lee - Wommack 230kV North | 112.25 | 102.34 | 103.54 | 110.04 | 107.56 | [14 empty] | 92.1 | [5 empty] | 103.77 | 93.26 | 94.54 | 100.77 | 98.1 | [15 empty] | 90.12 |  |  |  |  | 106.18 | 95.99 | 97.24 | 103.81 | 101.1 | [104 empty] | 0 | 112.25 | 5 | 2 | 3 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 10 | NO |  |  |  |  | Yes | 0 | No
304247,304251,1 | 230 | 304247 GA PAC TAP 230 304251 LEESUB230 TT 230 1 | Line | Lee - Wommack 230kV South | 130.02 | 116.7 | 118.01 | 126.34 | 123.41 |  |  |  |  | 92.13 | [9 empty] | 111.86 | 98 | 97.95 | 106.59 | 103.35 |  | 120.14 | 106.29 | 107.7 | 115.56 | 112.48 | [15 empty] | 108.17 | 93.99 | 93.93 | 102.75 | 99.16 | 123.67 | 110.22 | 111.6 | 119.79 | 116.72 | [15 empty] | 101.6 |  |  | 97.02 | 93.55 | [84 empty] | 0 | 130.02 | 8 | 7 | 6 | 0 | 0 | 0 | 8 | 7 | 6 | 3 | 15 | NO |  |  |  | 7652.31 | Yes | 8 | No
304500,305450,1 | 230 | 304500 WOMMACK230TT 230 305450 SANDYBSOLTAP 230 1 | Line | Lee - Wommack 230kV South | 112.17 | 99.81 | 101.12 | 109.17 | 106.51 | [14 empty] | 103.48 | 90.43 | 90.39 | 98.78 | 95.82 |  | 102.31 |  | 90.86 | 98.47 | 95.67 | [15 empty] | 99.8 |  |  | 94.89 | 91.71 | 105.81 | 93.23 | 94.61 | 102.58 | 99.74 | [15 empty] | 92.91 | [88 empty] | 0 | 112.17 | 5 | 1 | 2 | 0 | 0 | 0 | 5 | 1 | 2 | 3 | 7 | NO |  |  |  | 7492.31 | Yes | 8 | No
304247,305450,1 | 230 | 304247 GA PAC TAP 230 305450 SANDYBSOLTAP 230 1 | Line | Lee - Wommack 230kV South | 116.75 | 104.16 | 105.47 | 113.6 | 110.87 | [14 empty] | 105.86 | 92.6 | 92.55 | 101.01 | 97.99 |  | 106.89 | 93.77 | 95.19 | 102.86 | 100 | [15 empty] | 102.18 |  |  | 97.13 | 93.86 | 110.37 | 97.55 | 98.94 | 106.97 | 104.07 | [15 empty] | 95.3 |  |  | 91.17 | [85 empty] | 0 | 116.75 | 7 | 3 | 3 | 0 | 0 | 0 | 7 | 3 | 3 | 3 | 10 | NO |  |  |  |  | Yes | 0 | No
304030,305162,1 | 115 | 304030 LEESEP115WTT 115 305162 E17-ROSEWOOD 115 1 | Line | Lee Plant - Selma 115kV | 157.61 | 135.63 | 135.69 | 154.37 | 147.61 | 114.79 | 95.14 | 95.36 | 109.94 | 134.28 | 106.84 | 107.25 | 127.41 | 118.17 | 135.92 | 112.44 | 112.68 | 130.76 | 121.53 | 163.03 | 135.89 | 135.98 | 155.8 | 148.11 | 102.78 | 155.65 | 131.97 | 132.11 | 151.05 | 143.56 | 111.37 | 90.94 | 91.15 | 106.95 | 98.94 | 126.64 | 99.32 | 99.72 | 119.96 | 110.43 | 130.55 | 106.87 | 107.09 | 125.96 | 115.88 | 157.31 | 130.57 | 130.72 | 151 | 142.72 | 160.46 | 137.86 | 138.07 | 156.7 | 149.82 | 130.56 | 105.15 | 105.59 | 125.4 | 116.77 | 137.26 | 110.25 | 110.66 | 130.74 | 122.03 | 163.62 | 134.98 | 135.5 | 157.25 | 147.46 | 206.49 | 164.04 | 164.64 | 193.98 | 182 | [14 empty] | 103.45 | 103.33 | 90.9 | 91.15 | 100.73 | 96.46 | 103.33 | 98.32 | 98.23 |  |  | 94.98 | 90.83 | 98.23 | [12 empty] | 105.54 | 105.42 | 92.46 | 92.7 | 103.02 | 97.88 | 105.42 | 101.72 | 101.62 |  |  | 98.57 | 93.31 | 101.61 |  |  | 104.09 | 103.95 |  |  | 100.43 | 95.85 | 103.94 | 114.47 | 114.34 | 91.42 | 91.68 | 108.7 | 100.83 | 114.34 | 114.88 | 114.75 | 100.86 | 101.14 | 112.14 | 107.11 | 114.75 | 125.5 | 125.42 | 100.28 | 100.59 | 119.34 | 111.1 | 125.37 | 130.56 | 206.49 | 23 | 20 | 25 | 4 | 7 | 14 | 27 | 27 | 39 | 3 | 28 | NO |  |  | 120.76 | 8491.49 | Yes | 10 | No
304252,304302,1 | 115 | 304252 PRINCETON 115 304302 KENLY TAP 115 1 | Line | Lee Plant - Selma 115kV | 149.91 | 127.6 | 127.67 | 146.32 | 139.5 | 100.51 |  |  | 95.39 | 122.24 | 94.64 | 95.05 | 115.1 | 105.85 | 119.24 | 95.03 | 95.26 | 113.83 | 104.56 | 148.39 | 121.23 | 121.34 | 140.86 | 133.28 |  | 147.87 | 123.79 | 123.93 | 142.81 | 135.27 | 96.97 |  |  | 92.18 |  | 114.57 |  |  | 107.54 | 98 | 113.73 |  |  | 108.76 | 98.78 | 142.53 | 115.79 | 115.94 | 135.83 | 127.72 | 152.7 | 129.73 | 129.94 | 148.55 | 141.59 | 116.18 | 90.54 | 90.97 | 110.75 | 102.08 | 125.17 | 97.98 | 98.39 | 118.38 | 109.65 | 146.7 | 118.03 | 118.55 | 140.07 | 130.38 | 191.3 | 149.27 | 149.87 | 178.73 | 166.97 | [63 empty] | 91.65 | 91.53 |  |  |  |  | 91.52 | [7 empty] | 99.64 | 99.57 |  |  | 93.74 |  | 99.51 | 116.18 | 191.3 | 17 | 14 | 21 | 0 | 0 | 0 | 17 | 14 | 21 | 3 | 19 | NO |  |  | 109.81 | 8491.49 | Yes | 10 | No
304252,305162,1 | 115 | 304252 PRINCETON 115 305162 E17-ROSEWOOD 115 1 | Line | Lee Plant - Selma 115kV | 152.68 | 130.71 | 130.77 | 149.42 | 142.67 | 109.1 |  |  | 104.22 | 129.28 | 101.87 | 102.29 | 122.39 | 113.17 | 129.46 | 105.84 | 106.07 | 124.29 | 115.06 | 157.2 | 130.11 | 130.21 | 149.89 | 142.27 | 97.08 | 150.69 | 127.02 | 127.16 | 146.04 | 138.58 | 105.64 |  |  | 101.17 | 93.17 | 121.63 | 94.31 | 94.72 | 114.92 | 105.41 | 124.05 | 100.25 | 100.47 | 119.41 | 109.38 | 151.44 | 124.77 | 124.91 | 145.03 | 136.83 | 155.5 | 132.91 | 133.13 | 151.71 | 144.84 | 124.83 | 99.42 | 99.85 | 119.64 | 111.02 | 132.24 | 105.25 | 105.66 | 125.7 | 117 | 157.08 | 128.49 | 129.02 | 150.69 | 140.94 | 200.44 | 158.22 | 158.82 | 187.99 | 176.11 | [63 empty] | 96.68 | 96.56 |  |  | 91.54 |  | 96.56 | 95.57 | 95.45 |  |  | 93.05 |  | 95.45 | 105.76 | 105.69 |  |  | 100.26 | 92.96 | 105.64 | 124.83 | 200.44 | 22 | 20 | 23 | 0 | 0 | 4 | 22 | 20 | 27 | 3 | 22 | NO |  |  | 113.06 |  | Yes | 1 | No
304177,304302,1 | 115 | 304177 SELMA 115 TT 115 304302 KENLY TAP 115 1 | Line | Lee Plant - Selma 115kV | 140.61 | 118.38 | 118.44 | 137.03 | 130.25 | 90.77 |  |  |  | 113.6 |  |  | 106.48 | 97.27 | 108.29 |  |  | 102.88 | 93.62 | 138.41 | 111.42 | 111.53 | 130.87 | 123.39 |  | 138.48 | 114.49 | 114.63 | 133.4 | 125.94 | [5 empty] | 105.9 |  |  | 98.85 |  | 102.68 |  |  | 97.62 |  | 132.43 | 105.89 | 106.04 | 125.65 | 117.72 | 143.33 | 120.43 | 120.65 | 139.18 | 132.26 | 106.36 |  |  | 100.93 | 92.27 | 116.49 |  |  | 109.7 | 101.01 | 135.59 | 107.07 | 107.59 | 128.92 | 119.37 | 180.95 | 139.37 | 139.96 | 168.49 | 156.92 | [84 empty] | 106.36 | 180.95 | 14 | 12 | 20 | 0 | 0 | 0 | 14 | 12 | 20 | 3 | 17 | NO |  |  | 105 |  | Yes | 1 | No
304163,304174,1 | 115 | 304163 MILBUR115STT 115 304174 GARN PERSTOP 115 1 | Line | Method - Milburnie 115kV South | 102.39 | 94.79 | 94.87 | 106.32 | 99.03 |  |  |  | 91.54 |  |  |  | 92.23 |  | 99.63 | 92.31 | 92.39 | 103.16 | 95.92 | 104.7 | 95.68 | 95.75 | 107.7 | 100.24 |  | 103.34 | 94.62 | 94.7 | 106.85 | 98.79 | 91.14 |  |  | 95.56 |  |  |  |  | 91.23 |  | 100.79 | 93.25 | 93.31 | 105.18 | 96.75 | 105.85 | 95.93 | 95.96 | 109.19 | 100.53 | 100.78 | 92.79 | 92.89 | 104.38 | 97.04 | 92.59 |  |  | 96.34 |  |  |  |  | 92.11 |  | 106.72 | 98.74 | 98.82 | 110.6 | 102.56 | 113 | 102.23 | 102.35 | 115.49 | 107.14 | [84 empty] | 96.34 | 115.49 | 6 | 7 | 10 | 0 | 0 | 0 | 6 | 7 | 10 | 3 | 6 | YES |  |  | 107.01 |  | Yes | 2 | No
304152,304174,1 | 115 | 304152 GARNER 115 304174 GARN PERSTOP 115 1 | Line | Method - Milburnie 115kV South | 98.26 | 90.76 | 90.84 | 102.12 | 94.94 | [9 empty] | 95.37 |  |  | 98.84 | 91.71 | 100.45 | 91.54 | 91.62 | 103.38 | 96.04 |  | 99.1 | 90.52 | 90.6 | 102.51 | 94.62 |  |  |  | 91.32 | [6 empty] | 96.43 |  |  | 100.73 | 92.46 | 101.49 | 91.74 | 91.78 | 104.76 | 96.27 | 96.62 |  |  | 100.14 | 92.93 |  |  |  | 92.15 | [6 empty] | 102.32 | 94.48 | 94.56 | 106.13 | 98.26 | 108.57 | 98.01 | 98.13 | 111.04 | 102.83 | [84 empty] | 92.15 | 111.04 | 3 | 4 | 6 | 0 | 0 | 0 | 3 | 4 | 6 | 3 | 3 | YES |  |  | 102.6 |  | Yes | 2 | No
304131,304162,1 | 230 | 304131 RAL WORTHDAL 230 304162 MILBUR230 TT 230 1 | Line | Method - Milburnie 230kV | 96.17 |  |  | 100.97 | 90.27 | [14 empty] | 101.66 |  |  | 100.94 | 94.15 |  | 95.63 |  |  | 100.11 | [16 empty] | 94.64 |  |  | 100.58 |  | 92.92 |  |  | 95.63 | [11 empty] | 91.11 |  |  | 95.38 |  | 103.18 |  |  | 107.98 | 95.67 | [84 empty] | 0 | 107.98 | 3 | 2 | 2 | 0 | 0 | 0 | 3 | 2 | 2 | 3 | 2 | NO |  |  |  |  | Yes | 0 | No
304156,304190,1 | 230 | 304156 ROL/SQD TAP 230 304190 WAKE 230 TT 230 1 | Line | Milburnie - Wake 230kV | 101.36 | 96.18 | 96.24 | 104.94 | 99.37 | 98.95 | 94.19 | 94.25 | 102.2 | 105.52 | 100.15 | 100.08 | 107.99 | 102.52 | 112.3 | 107.3 | 107.37 | 115.58 | 110.02 | 114.11 | 107.68 | 107.67 | 116.88 | 111.03 | 96.91 | 95.06 |  |  | 98.64 | 92.07 | 94.02 |  |  | 98.2 | 92.05 | 94.38 |  |  | 97.6 | 91.83 | 104.34 | 99.46 | 99.52 | 108.37 | 102.13 | 105.92 | 99.18 | 99.18 | 109.18 | 102.68 | 91.25 |  |  | 94.87 |  | 94.13 |  |  | 97.95 | 92.52 | 95.78 | 90.66 | 90.72 | 98.84 | 93.49 | 108.53 | 103.28 | 103.36 | 112.3 | 106.27 | 109.33 | 101.72 | 101.74 | 112.04 | 105.54 | [84 empty] | 102.2 | 116.88 | 18 | 6 | 10 | 0 | 0 | 0 | 18 | 6 | 10 | 3 | 3 | NO |  |  |  |  | Yes | 0 | Yes
304465,304506,1 | 230 | 304465 NEWBERN230TT 230 304506 DOVER 230 1 | Line | New Bern - Wommack 230kV North | 213.54 | 187.76 | 190.37 | 206.77 | 201.62 | 177.34 | 149.15 | 151.76 | 167.67 | 183.19 | 154.27 | 156.77 | 172.56 | 166.74 | 166.51 | 139.44 | 141.99 | 158.08 | 152.83 | 225.9 | 196.97 | 196.94 | 215.23 | 208.87 | 162.09 | 208.66 | 181.27 | 184 | 199.98 | 194.45 | 176.66 | 147.34 | 149.94 | 165.87 | 159.94 | 181.83 | 151.52 | 153.96 | 169.76 | 163.56 | 165.32 | 137.37 | 140 | 155.84 | 150.33 | 224.6 | 194.4 | 194.36 | 212.62 | 206.08 | 197.62 | 171.84 | 174.49 | 190.37 | 185.17 | 165.18 | 138.63 | 141.2 | 156.82 | 151.47 | 173.23 | 145.93 | 148.4 | 163.87 | 158.26 | 164.18 | 138.29 | 140.9 | 156.51 | 151.41 | 205.88 | 178.39 | 178.51 | 196.21 | 190.1 | 144.81 | 144.72 | 115.94 | 118.68 | 136.42 | 130.59 | 144.73 | 150.69 | 150.62 | 121.19 | 123.9 | 141.35 | 135.22 | 150.63 | 126.16 | 126.09 | 98.72 | 101.43 | 119.23 | 113.81 | 126.1 | 191.33 | 191.23 | 163.69 | 163.77 | 182.46 | 176.08 | 191.24 | 146.86 | 146.79 | 116.45 | 119.13 | 136.82 | 152.41 | 152.33 | 121.16 | 123.83 | 141.01 | 134.48 | 152.34 | 127.26 | 127.18 | 98.61 | 101.31 | 118.99 | 113.21 | 127.19 | 193.18 | 193.08 | 163.93 | 163.97 | 182.75 | 175.85 | 193.1 | 130.56 | 146.8 | 143.07 | 143 | 115.39 | 118.16 | 135.45 | 129.7 | 143.01 | 152.17 | 152.09 | 123.76 | 126.5 | 143.52 | 137.5 | 152.1 | 135.88 | 135.8 | 108.84 | 111.61 | 129.05 | 123.54 | 135.82 | 181.78 | 181.68 | 154.52 | 154.57 | 173.08 | 166.9 | 181.71 | 177.34 | 225.9 | 25 | 25 | 25 | 13 | 15 | 14 | 38 | 40 | 39 | 3 | 50 | NO |  |  |  | 7283.58 | Yes | 8 | No
304500,304506,1 | 230 | 304500 WOMMACK230TT 230 304506 DOVER 230 1 | Line | New Bern - Wommack 230kV North | 214.81 | 188.88 | 191.49 | 207.91 | 202.73 | 176.65 | 148.34 | 150.96 | 166.89 | 182.79 | 153.73 | 156.23 | 172.05 | 166.2 | 165.55 | 138.36 | 140.91 | 157.03 | 151.76 | 225.21 | 196.23 | 196.2 | 214.47 | 208.1 | 161.28 | 209.93 | 182.37 | 185.1 | 201.09 | 195.53 | 175.98 | 146.53 | 149.13 | 165.09 | 159.13 | 181.43 | 150.97 | 153.42 | 169.24 | 163.01 | 164.36 | 136.29 | 138.92 | 154.78 | 149.25 | 223.9 | 193.65 | 193.61 | 211.84 | 205.3 | 198.88 | 172.94 | 175.59 | 191.5 | 186.26 | 164.48 | 137.81 | 140.39 | 156.03 | 150.65 | 172.81 | 145.38 | 147.86 | 163.36 | 157.71 | 163.22 | 137.22 | 139.83 | 155.46 | 150.33 | 205.18 | 177.63 | 177.75 | 195.46 | 189.34 | 116.3 | 116.22 | 92.58 | 94.84 | 109.41 | 104.62 | 116.23 | 121.43 | 121.37 | 97.19 | 99.42 | 113.75 | 108.72 | 121.38 | 100.68 | 100.62 |  |  | 94.99 | 90.54 | 100.63 | 154.44 | 154.36 | 131.79 | 131.85 | 147.17 | 141.95 | 154.38 | 117.98 | 117.92 | 93.01 | 95.2 | 109.74 | 122.84 | 122.77 | 97.17 | 99.36 | 113.47 | 108.11 | 122.78 | 101.58 | 101.52 |  |  | 94.8 | 90.05 | 101.53 | 155.97 | 155.89 | 131.99 | 132.02 | 147.41 | 141.77 | 155.9 | 104.59 | 117.93 | 114.86 | 114.8 | 92.13 | 94.4 | 108.61 | 103.89 | 114.81 | 122.63 | 122.57 | 99.3 | 101.56 | 115.54 | 110.59 | 122.58 | 108.66 | 108.59 |  |  | 103.06 | 98.53 | 108.61 | 146.6 | 146.52 | 124.27 | 124.31 | 139.47 | 134.41 | 146.54 | 176.65 | 225.21 | 25 | 25 | 25 | 10 | 12 | 11 | 35 | 37 | 36 | 3 | 44 | NO |  |  |  |  | Yes | 0 | No
304465,305524,1 | 230 | 304465 NEWBERN230TT 230 305524 Q424 230 1 | Line | New Bern - Wommack 230kV South | 148.8 | 134.84 | 136.11 | 144.09 | 141.19 | 133.6 | 117.07 | 118.3 | 126.11 | 137.36 | 120.11 | 121.33 | 129.07 | 125.36 | 126.65 | 110.84 | 112.06 | 119.97 | 116.66 | 156.17 | 140.33 | 140.28 | 148.8 | 145.01 | 122.59 | 148.04 | 132.94 | 134.19 | 142.16 | 138.9 | 133.62 | 116.18 | 117.64 | 125.49 | 121.75 | 137.03 | 118.61 | 119.98 | 127.92 | 123.95 | 126.27 | 110.14 | 111.36 | 119.18 | 115.74 | 155.89 | 139.31 | 139.36 | 147.82 | 143.9 | 145.14 | 131.08 | 132.38 | 140.31 | 137.17 | 129.5 | 113.68 | 114.89 | 122.89 | 119.36 | 134.63 | 118.08 | 119.33 | 127.11 | 123.52 | 127.31 | 112.03 | 113.34 | 121.06 | 117.79 | 148.11 | 132.7 | 132.72 | 141.1 | 137.44 | 105.13 | 105.09 | 90.33 | 91.43 | 99.12 | 95.76 | 105.1 | 108.43 | 108.4 | 92.82 | 93.87 | 101.65 | 98.1 | 108.4 | 95.7 | 95.67 |  |  | 90.5 |  | 95.68 | 124.66 | 124.62 | 110.8 | 110.74 | 118.5 | 115.01 | 124.62 | 105 | 104.97 |  | 90.53 | 97.96 | 108.23 | 108.2 | 91.31 | 92.45 | 100.17 | 96.33 | 108.2 | 95.16 | 95.14 |  |  |  |  | 95.14 | 124.34 | 124.3 | 109.69 | 109.59 | 117.35 | 113.83 | 124.31 | 94.35 | 104.98 | 103.78 | 103.75 |  | 90.86 | 98.16 | 94.89 | 103.75 | 108.59 | 108.56 | 93.63 | 94.71 | 102.38 | 98.92 | 108.56 | 99.43 | 99.4 |  |  | 94.34 | 91.23 | 99.4 | 120.16 | 120.11 | 106.43 | 106.28 | 114.29 | 110.87 | 120.12 | 133.62 | 156.17 | 25 | 25 | 25 | 7 | 8 | 7 | 32 | 33 | 32 | 3 | 38 | NO |  |  |  | 6856.08 | Yes | 7 | No
304500,305524,1 | 230 | 304500 WOMMACK230TT 230 305524 Q424 230 1 | Line | New Bern - Wommack 230kV South | 159.39 | 144.92 | 146.11 | 154.29 | 151.22 | 138.98 | 122.77 | 124 | 131.86 | 142.43 | 125.79 | 127.01 | 134.81 | 131.01 | 132.42 | 116.53 | 117.75 | 125.72 | 122.32 | 161.25 | 144.99 | 144.94 | 153.59 | 149.7 | 128.25 | 158.72 | 142.99 | 144.25 | 152.38 | 148.94 | 138.89 | 121.85 | 123.31 | 130.98 | 127.38 | 141.94 | 124.25 | 125.63 | 133.41 | 129.55 | 131.87 | 115.8 | 117.03 | 124.89 | 121.37 | 161.03 | 144 | 144.05 | 152.65 | 148.6 | 155.78 | 141.11 | 142.42 | 150.52 | 147.22 | 135.22 | 119.38 | 120.59 | 128.65 | 125.04 | 139.97 | 123.78 | 125.03 | 132.87 | 129.18 | 132.62 | 117.74 | 119.05 | 126.82 | 123.48 | 153.29 | 137.74 | 137.75 | 145.91 | 142.11 | 105.13 | 105.09 | 90.33 | 91.43 | 99.12 | 95.76 | 105.1 | 108.43 | 108.4 | 92.82 | 93.87 | 101.65 | 98.1 | 108.4 | 95.7 | 95.67 |  |  | 90.5 |  | 95.68 | 124.66 | 124.62 | 110.8 | 110.74 | 118.5 | 115.01 | 124.62 | 105 | 104.97 |  | 90.53 | 97.96 | 108.23 | 108.2 | 91.31 | 92.45 | 100.17 | 96.33 | 108.2 | 95.16 | 95.14 |  |  |  |  | 95.14 | 124.34 | 124.3 | 109.69 | 109.59 | 117.35 | 113.83 | 124.31 | 94.35 | 104.98 | 103.78 | 103.75 |  | 90.86 | 98.16 | 94.89 | 103.75 | 108.59 | 108.56 | 93.63 | 94.71 | 102.38 | 98.92 | 108.56 | 99.43 | 99.4 |  |  | 94.34 | 91.23 | 99.4 | 120.15 | 120.11 | 106.43 | 106.28 | 114.29 | 110.87 | 120.12 | 138.98 | 161.25 | 25 | 25 | 25 | 7 | 8 | 7 | 32 | 33 | 32 | 3 | 38 | NO |  |  |  |  | Yes | 0 | No
304465,304466,1 | 230 | 304465 NEWBERN230TT 230 304466 NEWBER115NTT 115 1 | Substation | New Bern 230kV | 187.63 | 188.51 | 187.63 | 183.35 | 182.89 | 188.32 | 187.85 | 186.94 | 182.1 | 180.33 | 178.75 | 177.74 | 173.49 | 172.47 | 197.12 | 197.45 | 196.23 | 191.98 | 191.16 | 175.11 | 174.24 | 174.18 | 170.6 | 169.81 | 181.24 | 187.55 | 187.48 | 186.59 | 181.89 | 181.24 | 189.28 | 188.2 | 187.3 | 182.56 | 181.46 | 181.29 | 179.1 | 178.13 | 173.84 | 172.65 | 198.08 | 197.73 | 196.86 | 191.79 | 190.79 | 176.67 | 174.13 | 174.77 | 170.28 | 170.23 | 186.81 | 187.22 | 186.38 | 181.78 | 181.39 | 189.34 | 189.21 | 188.32 | 183.4 | 182.71 | 180.32 | 179.74 | 178.81 | 174.29 | 173.47 | 194.73 | 195.1 | 194.1 | 190.07 | 189.28 | 177.81 | 175.65 | 175.62 | 171.9 | 170.99 | 198.04 | 198.06 | 198.24 | 197.23 | 191.94 | 191.04 | 198.06 | 189.4 | 189.42 | 188.58 | 187.47 | 182.55 | 181.48 | 189.42 | 210.34 | 210.36 | 209.72 | 208.69 | 204.39 | 203.63 | 210.36 | 184.42 | 184.44 | 183.81 | 183.67 | 179.48 | 178.81 | 184.44 | 199.15 | 199.17 | 198.21 | 197.1 | 192.28 | 190.89 | 190.45 | 188.7 | 187.57 | 183.13 | 181.83 | 190.45 | 211.52 | 211.55 | 211.2 | 210.05 | 204.95 | 203.9 | 211.54 | 185.95 | 185.96 | 183.97 | 183.71 | 179.94 | 178.91 | 185.96 | 191.16 | 199.17 | 197.72 | 197.74 | 197.66 | 196.55 | 191.88 | 191.08 | 197.74 | 188.66 | 188.68 | 187.74 | 186.43 | 182.3 | 181.33 | 188.68 | 206.28 | 206.3 | 207.38 | 206.18 | 200.77 | 200.05 | 206.3 | 186.66 | 186.68 | 185.59 | 185.43 | 181.45 | 180.8 | 186.67 | 199.17 | 211.55 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | YES |  |  |  | 3397.34 | Yes | 5 | No
304465,304489,2 | 230 | 304465 NEWBERN230TT 230 304489 NEWBER115STT 115 2 | Substation | New Bern 230kV | 167.38 | 168.17 | 167.39 | 163.57 | 163.16 | 167.99 | 167.59 | 166.77 | 162.45 | 160.86 | 159.46 | 158.56 | 154.77 | 153.87 | 175.84 | 176.14 | 175.05 | 171.26 | 170.53 | 156.21 | 155.44 | 155.38 | 152.19 | 151.49 | 161.69 | 167.31 | 167.25 | 166.46 | 162.26 | 161.69 | 168.85 | 167.9 | 167.1 | 162.86 | 161.88 | 161.73 | 159.77 | 158.91 | 155.08 | 154.03 | 176.69 | 176.39 | 175.62 | 171.08 | 170.19 | 157.61 | 155.34 | 155.91 | 151.9 | 151.86 | 166.65 | 167.03 | 166.27 | 162.17 | 161.82 | 168.9 | 168.8 | 168.01 | 163.61 | 162.99 | 160.85 | 160.35 | 159.52 | 155.49 | 154.75 | 174.63 | 174.05 | 173.15 | 169.55 | 168.85 | 158.62 | 156.69 | 156.67 | 153.35 | 152.54 | 176.67 | 176.69 | 176.84 | 175.94 | 171.23 | 170.43 | 176.69 | 168.96 | 168.98 | 168.24 | 167.25 | 163.22 | 162.27 | 168.98 | 187.63 | 187.65 | 187.09 | 186.15 | 182.33 | 181.64 | 187.65 | 164.52 | 164.54 | 163.86 | 163.85 | 160.11 | 159.52 | 164.54 | 177.66 | 177.68 | 176.81 | 175.82 | 171.53 | 170.3 | 170.32 | 168.34 | 167.33 | 163.37 | 162.21 | 170.32 | 188.68 | 188.71 | 188.4 | 187.37 | 182.82 | 181.89 | 188.7 | 165.88 | 165.87 | 164.11 | 163.88 | 160.52 | 159.6 | 165.9 | 170.53 | 177.67 | 176.38 | 176.4 | 176.33 | 175.34 | 171.17 | 170.46 | 176.4 | 168.31 | 168.33 | 167.49 | 166.31 | 162.62 | 161.76 | 168.32 | 184.01 | 184.03 | 184.99 | 183.92 | 179.1 | 178.45 | 184.02 | 166.52 | 166.54 | 165.56 | 165.42 | 161.87 | 161.08 | 166.53 | 177.68 | 188.71 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | YES |  |  |  | 3397.34 | Yes | 5 | No
304466,304489,Z1 | 115 | 304466 NEWBER115NTT 115 304489 NEWBER115STT 115 Z1 | Substation | New Bern 230kV | 148.36 | 149.06 | 148.36 | 144.97 | 144.61 | 148.9 | 148.54 | 147.81 | 143.99 | 142.58 | 141.34 | 140.54 | 137.18 | 136.38 | 155.87 | 156.12 | 155.16 | 151.79 | 151.14 | 138.45 | 137.76 | 137.71 | 134.87 | 134.25 | 143.31 | 148.3 | 148.25 | 147.54 | 143.82 | 143.31 | 149.66 | 148.82 | 148.1 | 144.35 | 143.48 | 143.34 | 141.61 | 140.85 | 137.45 | 136.51 | 156.62 | 156.34 | 155.66 | 151.65 | 150.86 | 139.64 | 137.68 | 138.17 | 134.62 | 134.56 | 147.71 | 148.04 | 147.37 | 143.73 | 143.43 | 149.71 | 149.61 | 148.91 | 145.02 | 144.47 | 142.58 | 142.13 | 141.39 | 137.81 | 137.16 | 154.75 | 154.28 | 153.48 | 150.28 | 149.66 | 140.54 | 138.88 | 138.86 | 135.91 | 135.19 | 156.59 | 156.61 | 156.74 | 155.94 | 151.76 | 151.05 | 156.61 | 149.76 | 149.78 | 149.11 | 148.23 | 144.66 | 143.81 | 149.77 | 166.3 | 166.32 | 165.83 | 165 | 161.6 | 160.99 | 166.32 | 145.81 | 145.83 | 145.22 | 145.22 | 141.9 | 141.37 | 145.83 | 157.47 | 157.49 | 156.71 | 155.84 | 152.03 | 150.94 | 150.96 | 149.2 | 148.31 | 144.79 | 143.77 | 150.96 | 167.24 | 167.26 | 166.98 | 166.07 | 162.04 | 161.21 | 167.25 | 147.02 | 147.01 | 145.45 | 145.25 | 142.26 | 141.44 | 147.03 | 151.15 | 157.48 | 156.34 | 156.36 | 156.29 | 155.41 | 151.71 | 151.08 | 156.35 | 149.17 | 149.19 | 148.44 | 147.41 | 144.13 | 143.36 | 149.18 | 163.09 | 163.11 | 163.96 | 163.02 | 158.74 | 158.17 | 163.11 | 147.59 | 147.6 | 146.73 | 146.61 | 143.46 | 142.76 | 147.59 | 157.49 | 167.26 | 25 | 25 | 25 | 14 | 16 | 14 | 39 | 41 | 39 | 3 | 50 | YES |  |  |  |  | Yes | 1 | No
304723,900035,1 | 115 | 304723 CAMDENJCT TT 115 900035 ID_569014 115 1 | Line | Robinson Plant - Camden Junction 115kV | [25 empty] | 98.02 | 90.06 |  | 93.03 |  | 93.49 | [14 empty] | 103.99 | 96.96 | 96.85 | 99.76 |  | 112.3 | 104.77 | 104.7 | 107.64 | 92.84 | 110.87 | 103.88 | 103.81 | 106.57 | 91.6 | 103.38 | 96.18 | 96.1 | 98.88 |  | 100.1 | 93.4 | 93.33 | 96.07 |  | 118.57 | 111.6 | 111.5 | 114.39 | 99.89 | [84 empty] | 110.87 | 118.57 | 0 | 1 | 14 | 0 | 0 | 0 | 0 | 1 | 14 | 2 | 8 | NO |  |  | 104.61 |  | Yes | 1 | No
Note on GA5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## NSuttonOFW
North Sutton OFW Cluster
| Exclusion Criteria |  |  |  | Scenario 1 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 2 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 3 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 1 - Winter Cases - Max Branch Loading [%] | [27 empty] | Scenario 2 - Winter Cases - Max Branch Loading [%] | [25 empty] | Scenario 3 - Winter Cases - Max Branch Loading [%] | [29 empty] | 170 | [10 empty] | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Progress Overloads |  |  |  |  | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Max Base [%] | Max Overload [%] | Cases with Overloads | [8 empty] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results |  | 190
Branch Identifier | Voltage | Monitored Branch | Line or Substation | Branch Name | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_CSM_br1dn | ctpc34s_r3_MVST_Scenario1_CSM_br2dn | ctpc34s_r3_MVST_Scenario1_CSM_hardn | ctpc34s_r3_MVST_Scenario1_CSM_rob2dn | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_SP_br1dn | ctpc34s_r3_MVST_Scenario1_SP_br2dn | ctpc34s_r3_MVST_Scenario1_SP_hardn | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_S90_br1dn | ctpc34s_r3_MVST_Scenario1_S90_br2dn | ctpc34s_r3_MVST_Scenario1_S90_hardn | ctpc34s_r3_MVST_Scenario1_S90_rob2dn | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S110_br1dn | ctpc34s_r3_MVST_Scenario1_S110_br2dn | ctpc34s_r3_MVST_Scenario1_S110_hardn | ctpc34s_r3_MVST_Scenario1_S110_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario1_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario1_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_CSM_br1dn | ctpc34s_r3_MVST_Scenario2_CSM_br2dn | ctpc34s_r3_MVST_Scenario2_CSM_hardn | ctpc34s_r3_MVST_Scenario2_CSM_rob2dn | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_SP_br1dn | ctpc34s_r3_MVST_Scenario2_SP_br2dn | ctpc34s_r3_MVST_Scenario2_SP_hardn | ctpc34s_r3_MVST_Scenario2_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_S90_br1dn | ctpc34s_r3_MVST_Scenario2_S90_br2dn | ctpc34s_r3_MVST_Scenario2_S90_hardn | ctpc34s_r3_MVST_Scenario2_S90_rob2dn | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S110_br1dn | ctpc34s_r3_MVST_Scenario2_S110_br2dn | ctpc34s_r3_MVST_Scenario2_S110_hardn | ctpc34s_r3_MVST_Scenario2_S110_rob2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario2_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario2_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_CSM_br1dn | ctpc34s_r3_MVST_Scenario3_CSM_br2dn | ctpc34s_r3_MVST_Scenario3_CSM_hardn | ctpc34s_r3_MVST_Scenario3_CSM_rob2dn | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_SP_br1dn | ctpc34s_r3_MVST_Scenario3_SP_br2dn | ctpc34s_r3_MVST_Scenario3_SP_hardn | ctpc34s_r3_MVST_Scenario3_SP_rob2dn | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_S90_br1dn | ctpc34s_r3_MVST_Scenario3_S90_br2dn | ctpc34s_r3_MVST_Scenario3_S90_hardn | ctpc34s_r3_MVST_Scenario3_S90_rob2dn | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S110_br1dn | ctpc34s_r3_MVST_Scenario3_S110_br2dn | ctpc34s_r3_MVST_Scenario3_S110_hardn | ctpc34s_r3_MVST_Scenario3_S110_rob2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34s_r3_MVST_Scenario3_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario3_SP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_br1dn | ctpc34w_r3_MVST_Scenario1_WP_br2dn | ctpc34w_r3_MVST_Scenario1_WP_hardn | ctpc34w_r3_MVST_Scenario1_WP_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_waltdn | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W90_br1dn | ctpc34w_r3_MVST_Scenario1_W90_br2dn | ctpc34w_r3_MVST_Scenario1_W90_hardn | ctpc34w_r3_MVST_Scenario1_W90_rob2dn | ctpc34w_r3_MVST_Scenario1_W90_waltdn | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W110_br1dn | ctpc34w_r3_MVST_Scenario1_W110_br2dn | ctpc34w_r3_MVST_Scenario1_W110_hardn | ctpc34w_r3_MVST_Scenario1_W110_rob2dn | ctpc34w_r3_MVST_Scenario1_W110_waltdn | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario1_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario1_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_br1dn | ctpc34w_r3_MVST_Scenario2_WP_br2dn | ctpc34w_r3_MVST_Scenario2_WP_hardn | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W90_br1dn | ctpc34w_r3_MVST_Scenario2_W90_br2dn | ctpc34w_r3_MVST_Scenario2_W90_hardn | ctpc34w_r3_MVST_Scenario2_W90_rob2dn | ctpc34w_r3_MVST_Scenario2_W90_waltdn | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W110_br1dn | ctpc34w_r3_MVST_Scenario2_W110_br2dn | ctpc34w_r3_MVST_Scenario2_W110_hardn | ctpc34w_r3_MVST_Scenario2_W110_rob2dn | ctpc34w_r3_MVST_Scenario2_W110_waltdn | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario2_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_waltdn | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_br1dn | ctpc34w_r3_MVST_Scenario3_WP_br2dn | ctpc34w_r3_MVST_Scenario3_WP_hardn | ctpc34w_r3_MVST_Scenario3_WP_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_waltdn | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W90_br1dn | ctpc34w_r3_MVST_Scenario3_W90_br2dn | ctpc34w_r3_MVST_Scenario3_W90_hardn | ctpc34w_r3_MVST_Scenario3_W90_rob2dn | ctpc34w_r3_MVST_Scenario3_W90_waltdn | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W110_br1dn | ctpc34w_r3_MVST_Scenario3_W110_br2dn | ctpc34w_r3_MVST_Scenario3_W110_hardn | ctpc34w_r3_MVST_Scenario3_W110_rob2dn | ctpc34w_r3_MVST_Scenario3_W110_waltdn | ctpc34w_r3_MVST_Scenario3_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario3_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_waltdn | Total | Grand Total | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
304463,305142,1 | 230 | 304463 NEW BERN WES 230 305142 E16-FAIRFELD 230 1 | Line | Aurora SS - New Bern 230kV | 97.83 |  |  | 92.81 | 90.9 | 93.77 |  |  |  | 97.23 |  |  | 91.17 |  | 96.18 |  |  |  |  | 126.02 | 103.62 | 103.76 | 116.15 | 113.12 |  | 94.05 | [9 empty] | 93.19 |  |  |  |  | 90.25 |  |  |  |  | 118.76 | 96.83 | 96.97 | 108.77 | 105.56 | 93.01 |  |  |  |  | 92.56 |  |  |  |  | 95.58 |  |  |  |  | 100.91 |  |  | 93.08 | 90.86 | 127.74 | 103.19 | 103.44 | 117.14 | 113.4 | 90.48 | 90.44 |  |  |  |  | 90.46 | 94.12 | 94.08 |  |  |  |  | 94.1 | 92.74 | 92.66 |  |  |  |  | 92.71 | 113.47 | 113.4 | 96.65 | 96.74 | 105.56 | 103.46 | 113.43 | [5 empty] | 92.34 | 92.3 |  |  |  |  | 92.32 | 90.55 | 90.5 |  |  |  |  | 90.52 | 111.84 | 111.77 | 94.4 | 94.47 | 103.6 | 101.04 | 111.81 |  |  | 95.81 | 95.73 |  |  | 90.02 |  | 95.77 | 100.46 | 100.39 |  |  | 92.81 | 90.71 | 100.43 | 99.96 | 99.88 |  |  | 93.03 | 91 | 99.93 | 116.34 | 116.27 | 97.66 | 97.89 | 108.33 | 105.93 | 116.3 | 95.81 | 127.74 | 5 | 3 | 6 | 5 | 5 | 5 | 10 | 8 | 11 | 3 | 0 | NO |  |  |  | 7903.82 | Yes | 8 | No
304463,304465,1 | 230 | 304463 NEW BERN WES 230 304465 NEWBERN230TT 230 1 | Line | Aurora SS - New Bern 230kV | 96.68 |  |  | 91.84 |  | 95.4 |  |  |  | 98.3 |  |  | 92.38 | 90.14 | 98.41 |  |  | 91.18 |  | 127.69 | 105.44 | 105.58 | 117.97 | 114.97 |  | 92.89 |  |  |  |  | 91.47 |  |  |  |  | 94.24 |  |  |  |  | 92.44 |  |  |  |  | 120.43 | 98.63 | 98.77 | 110.6 | 107.42 | 91.85 |  |  |  |  | 94.18 |  |  |  |  | 96.64 |  |  | 90.91 |  | 103.16 |  |  | 95.45 | 93.25 | 129.42 | 105 | 105.26 | 118.95 | 115.25 | 93.87 | 93.83 |  |  |  |  | 93.85 | 97.05 | 97 |  |  | 90.94 |  | 97.02 | 96.58 | 96.5 |  |  | 91.09 |  | 96.54 | 116.81 | 116.74 | 100.05 | 100.15 | 108.95 | 106.86 | 116.77 | 92.21 | 92.17 |  |  |  | 95.26 | 95.22 |  |  |  |  | 95.24 | 94.39 | 94.34 |  |  |  |  | 94.37 | 115.19 | 115.12 | 97.81 | 97.89 | 106.99 | 104.45 | 115.15 |  | 92.19 | 99.19 | 99.11 |  |  | 93.43 | 91.48 | 99.15 | 103.38 | 103.31 |  |  | 95.77 | 93.68 | 103.34 | 103.79 | 103.71 |  |  | 96.9 | 94.87 | 103.75 | 119.66 | 119.6 | 101.07 | 101.29 | 111.71 | 109.33 | 119.62 | 99.19 | 129.42 | 5 | 3 | 6 | 7 | 5 | 10 | 12 | 8 | 16 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304434,305142,1 | 230 | 304434 BAYBORO TAP 230 305142 E16-FAIRFELD 230 1 | Line | Aurora SS - New Bern 230kV | 95.99 |  |  | 90.97 |  | 91.88 |  |  |  | 95.55 |  |  |  |  | 94.04 |  |  |  |  | 124.04 | 101.69 | 101.83 | 114.19 | 111.16 |  | 92.21 | [9 empty] | 91.51 | [9 empty] | 116.79 | 94.93 | 95.07 | 106.82 | 103.62 | 91.17 |  |  |  |  | 90.66 |  |  |  |  | 93.9 |  |  |  |  | 98.75 |  |  | 90.96 |  | 125.77 | 101.26 | 101.51 | 115.17 | 111.44 | [7 empty] | 91.93 | 91.88 |  |  |  |  | 91.9 | [7 empty] | 110.96 | 110.89 | 94.16 | 94.26 | 103.06 | 100.96 | 110.93 | [5 empty] | 90.15 | 90.11 |  |  |  |  | 90.13 | [7 empty] | 109.34 | 109.27 | 91.92 | 91.99 | 101.1 | 98.55 | 109.3 |  |  | 93.33 | 93.25 |  |  |  |  | 93.29 | 98.26 | 98.19 |  |  | 90.62 |  | 98.22 | 97.18 | 97.1 |  |  | 90.27 |  | 97.15 | 113.83 | 113.76 | 95.18 | 95.4 | 105.83 | 103.44 | 113.79 | 93.33 | 125.77 | 5 | 3 | 5 | 5 | 4 | 5 | 10 | 7 | 10 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304582,305010,1 | 230 | 304582 DELCO230 TT 230 305010 E1-BOLIVIA 230 1 | Line | Brunswick Unit 1 - Delco 230kV East | [16 empty] | 91.39 |  |  | 0 |  | 95.11 | 95.73 | 93.67 | [18 empty] | 90.12 |  |  | 0 |  | 94.49 | 95.23 | 93.05 | [20 empty] | 90.52 |  | 96.96 | 0 | 96.6 | [84 empty] | 0 | 96.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304022,305995,1 | 230 | 304022 BRUN1 230 TT 230 305995 6SUTNORTH230 230 1 | Line | Brunswick Unit 1 - Jacksonville 230kV | [19 empty] | 99.29 | 164.39 | 112.97 | 124.84 | 124.09 | [21 empty] | 100.96 | 165.15 | 113.87 | 125.92 | 124.92 | [20 empty] | 108.49 | 170.94 | 118.59 | 100.14 | 131.1 | [21 empty] | 0 | 0 | 130.27 |  | 94.11 | 93.81 | 0 | [19 empty] | 0 | 0 | 132.44 |  | 96.35 | 96.11 | 0 | [23 empty] | 0 | 0 | 134.26 |  | 98.31 | 97.8 | 0 | 0 | 170.94 | 4 | 5 | 5 | 1 | 1 | 1 | 5 | 6 | 6 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304022,304046,1 | 230 | 304022 BRUN1 230 TT 230 304046 WSPOON230 TT 230 1 | Line | Brunswick Unit 1 - Weatherspoon Plant 230kV | 90.6 | [18 empty] | 127.63 |  |  | 118.89 | 118.64 | [21 empty] | 130.68 |  | 91.98 | 121.07 | 120.57 | [20 empty] | 142.78 |  | 99.66 | 127.1 | 130.07 | [21 empty] | 93.99 | 94.14 |  |  |  |  | 94.12 | [19 empty] | 100.9 | 101.05 |  |  | 93.27 | 93.61 | 101.02 | [23 empty] | 104.25 | 104.34 |  |  | 95.96 | 96.27 | 104.3 | 0 | 142.78 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 6 | 6 | 3 | 0 | NO |  |  |  | 7520.46 | Yes | 8 | No
304020,305005,1 | 230 | 304020 BRUN2 230 TT 230 305005 E1-SOUTHPORT 230 1 | Line | Brunswick Unit 2 - Delco 230kV West |  | 90.58 |  |  |  |  | 94.91 |  |  |  | 92.89 |  |  |  |  | 97.38 |  |  |  | 108.83 | 108.69 |  | 109.74 | 107.04 | [7 empty] | 93.71 |  |  |  |  | 91.2 |  |  |  |  | 95.82 |  |  |  | 109.53 | 107.73 |  | 109.01 | 106.17 | 90.57 | [5 empty] | 92.78 |  |  |  |  | 90.37 | [8 empty] | 114.48 | 110.07 |  | 106.96 | 109.94 | [84 empty] | 94.91 | 114.48 | 4 | 4 | 4 | 0 | 0 | 0 | 4 | 4 | 4 | 3 | 0 | YES |  |  |  | 5651.88 | Yes | 7 | Yes
304582,305005,1 | 230 | 304582 DELCO230 TT 230 305005 E1-SOUTHPORT 230 1 | Line | Brunswick Unit 2 - Delco 230kV West | [19 empty] | 95.26 | 95.25 |  | 95.31 | 92.83 | [21 empty] | 95.93 | 94.29 |  | 94.53 | 91.96 | [20 empty] | 100.89 | 96.44 |  | 93.42 | 95.25 | [84 empty] | 0 | 100.89 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304020,305995,1 | 230 | 304020 BRUN2 230 TT 230 305995 6SUTNORTH230 230 1 | Line | Brunswick Unit 2 - Wallace 230kV | [19 empty] | 121.15 | 132.82 | 186.09 | 148.28 | 147.5 | [21 empty] | 123.13 | 133.88 | 187.14 | 149.59 | 148.51 | [20 empty] | 132.07 | 139.52 | 193.89 | 121.89 | 155.92 | [21 empty] | 95.52 | 95.58 | 102.47 | 149.48 | 115.49 | 115.12 | 95.57 | [19 empty] | 98.13 | 98.21 | 104.32 | 151.06 | 117.4 | 117.1 | 98.19 | [23 empty] | 100.85 | 100.93 | 106.36 | 153.94 | 120.25 | 119.65 | 100.91 | 0 | 193.89 | 5 | 5 | 5 | 4 | 4 | 7 | 9 | 9 | 12 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304515,305995,1 | 230 | 304515 WALLACE230TT 230 305995 6SUTNORTH230 230 1 | Line | Brunswick Unit 2 - Wallace 230kV | [19 empty] | 154.74 | 122.48 | 123.68 | 148.54 | 143.07 | [21 empty] | 153.12 | 119.37 | 121.15 | 146.24 | 140.68 | [20 empty] | 147.22 | 111.74 | 113.65 | 139.58 | 134.35 | [21 empty] | 131.85 | 131.73 | 103.52 | 104.85 | 127.58 | 122.45 | 131.74 | [19 empty] | 129.73 | 129.64 | 100.58 | 101.95 | 124.26 | 119.03 | 129.66 | [23 empty] | 127.16 | 127.07 | 98.29 | 99.68 | 122.18 | 117.27 | 127.09 | 0 | 154.74 | 5 | 5 | 5 | 7 | 7 | 5 | 12 | 12 | 10 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305004,305011,1 | 230 | 305004 E1-PROSPECT 230 305011 ROYALOAK 230 1 | Line | Brunswick Unit 2 - Whiteville 230kV | [19 empty] | 114.43 |  |  | 104.39 | 104.81 | [21 empty] | 117.47 |  |  | 106.61 | 106.81 | [20 empty] | 129.09 |  |  | 114.05 | 116.78 | [84 empty] | 0 | 129.09 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  | 6726.57 | Yes | 7 | No
304600,305011,1 | 230 | 304600 WHITEVL230TT 230 305011 ROYALOAK 230 1 | Line | Brunswick Unit 2 - Whiteville 230kV | [19 empty] | 113.84 |  |  | 102.74 | 103.16 | [21 empty] | 116.92 |  |  | 105.02 | 105.2 | [20 empty] | 128.9 |  |  | 113.51 | 115.31 | [84 empty] | 0 | 128.9 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304513,304533,1 | 115 | 304513 BURGAW SUB 115 304533 INDUSTR TAP 115 1 | Line | Castle Hayne - Wallace 115kV | [19 empty] | 114.45 |  |  | 112.81 | 107.97 | [21 empty] | 119.37 |  |  | 116.76 | 109.4 | [20 empty] | 95.81 |  |  | 94.4 | [22 empty] | 128.35 | 128.22 | 99.21 | 99.42 | 126.38 | 120.7 | 128.24 | [19 empty] | 111.35 | 111.21 |  |  | 109.45 | 103.61 | 111.24 | [23 empty] | 115.64 | 115.5 |  |  | 113.89 | 106.97 | 115.54 | 0 | 128.35 | 3 | 3 | 0 | 5 | 5 | 5 | 8 | 8 | 5 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304533,304545,1 | 115 | 304533 INDUSTR TAP 115 304545 CASTLH115WTT 115 1 | Line | Castle Hayne - Wallace 115kV | [19 empty] | 113.25 |  |  | 111.61 | 107.05 | [21 empty] | 118.36 | 90.77 | 90.76 | 115.87 | 109.23 | [20 empty] | 95.84 |  |  | 94.3 | [22 empty] | 112.94 | 112.82 |  |  | 111.3 | 106.59 | 112.84 | [19 empty] | 98.45 | 98.33 |  |  | 96.87 | 92 | 98.35 | [23 empty] | 102.44 | 102.33 |  |  | 100.98 | 95.58 | 102.36 | 0 | 118.36 | 3 | 3 | 0 | 5 | 0 | 4 | 8 | 3 | 4 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304511,304513,1 | 115 | 304511 WALLACE TAP 115 304513 BURGAW SUB 115 1 | Line | Castle Hayne - Wallace 115kV | [19 empty] | 99.55 |  |  | 97.81 | 93.39 | [21 empty] | 103.78 |  |  | 101.09 | 94.31 | [46 empty] | 91.93 | 91.82 |  |  | 90.37 |  | 91.84 | [56 empty] | 0 | 103.78 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304550,304545,1 | 230 | 304550 CASTLEH230TT 230 304545 CASTLH115WTT 115 1 | Substation | Castle Hayne 230kV | [19 empty] | 90.43 | [25 empty] | 90.71 | [50 empty] | 109.72 | 109.66 |  |  | 107.51 | 104.77 | 109.67 | [19 empty] | 105.7 | 105.63 |  |  | 103.22 | 100.3 | 105.65 | [23 empty] | 105.76 | 105.71 |  |  | 103.7 | 100.9 | 105.72 | 0 | 109.72 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 0 | NO |  |  |  | 2400.04 | Yes | 3 | No
304258,305130,1 | 115 | 304258 CLINTON NTH 115 305130 E15-HALLPOND 115 1 | Line | Clinton - Vander 115kV | [19 empty] | 92.71 | [25 empty] | 96.1 |  |  |  |  | 93.73 | [19 empty] | 123.42 | 93.51 | 93.78 | 111.81 | 109.77 | [84 empty] | 0 | 123.42 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | NO |  |  |  | 3869.55 | Yes | 4 | No
304260,305133,1 | 115 | 304260 ROSEBORO 115 305133 E15-STEDMAN 115 1 | Line | Clinton - Vander 115kV | [70 empty] | 107.41 |  |  | 95.89 | 94.06 | [84 empty] | 0 | 107.41 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | NO |  |  |  | 3869.55 | Yes | 4 | No
304260,305130,1 | 115 | 304260 ROSEBORO 115 305130 E15-HALLPOND 115 1 | Line | Clinton - Vander 115kV | [70 empty] | 115.44 |  |  | 103.96 | 102.04 | [84 empty] | 0 | 115.44 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304401,305133,1 | 115 | 304401 VANDERSUB TT 115 305133 E15-STEDMAN 115 1 | Line | Clinton - Vander 115kV | [70 empty] | 99.69 | [88 empty] | 0 | 99.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304505,305032,1 | 230 | 304505 ROSE HILL 230 305032 E4-BLIND BRG 230 1 | Line | Clinton - Wallace 230kV | [19 empty] | 142.44 | 106.23 | 105.7 | 136.49 | 130.43 | [21 empty] | 139.5 | 102.82 | 101.55 | 132.58 | 126.88 | [20 empty] | 134.33 | 96.9 | 95.28 | 127.29 | 121.53 | [21 empty] | 112.88 | 112.79 |  |  | 108.42 | 102.47 | 112.8 | [19 empty] | 116.4 | 116.32 |  |  | 110.56 | 104.29 | 116.33 | [23 empty] | 109.48 | 109.34 |  |  | 104.79 | 98.96 | 109.35 | 0 | 142.44 | 5 | 5 | 3 | 5 | 5 | 4 | 10 | 10 | 7 | 3 | 0 | NO |  |  |  | 6947.86 | Yes | 7 | No
304503,305032,1 | 230 | 304503 WARSAW TAP 230 305032 E4-BLIND BRG 230 1 | Line | Clinton - Wallace 230kV | 91.76 |  |  | 90.74 | [15 empty] | 166.4 | 123.84 | 123.22 | 159.41 | 152.29 | [21 empty] | 162.93 | 119.83 | 118.34 | 154.8 | 148.11 | [20 empty] | 156.85 | 112.87 | 110.96 | 148.57 | 141.81 | [21 empty] | 111.58 | 111.5 |  |  | 107.13 | 101.19 | 111.5 | [19 empty] | 115.09 | 115.01 |  |  | 109.26 | 103.01 | 115.02 | [23 empty] | 108.17 | 108.03 |  |  | 103.49 | 97.68 | 108.04 | 0 | 166.4 | 5 | 5 | 5 | 5 | 5 | 4 | 10 | 10 | 9 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304505,305031,1 | 230 | 304505 ROSE HILL 230 305031 E4-BEVERAGE 230 1 | Line | Clinton - Wallace 230kV | [19 empty] | 126.97 | 94.83 | 94.37 | 121.73 | 116.35 | [21 empty] | 124.35 | 91.82 | 90.68 | 118.26 | 113.21 | [20 empty] | 119.76 |  |  | 113.55 | 108.45 | [84 empty] | 0 | 126.97 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304205,304255,1 | 230 | 304205 CLINTON230TT 230 304255 CLINTON115TT 115 1 | Substation | Clinton 230kV | [19 empty] | 100.94 |  |  | 96.22 | 94.37 | [21 empty] | 100.89 |  |  | 95.75 | 94.06 | [20 empty] | 106.15 |  |  | 101.23 | 99.59 | [21 empty] | 94.69 | 94.68 |  |  |  | 90.53 | 94.69 | [19 empty] | 95.28 | 95.31 |  |  | 90.31 |  | 95.29 | [23 empty] | 95.62 | 95.65 |  |  | 91.09 |  | 95.62 | 0 | 106.15 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | NO |  |  |  | 3028.69 | Yes | 4 | No
305390,900005,1 | 230 | 305390 ROWANSOL-TAP 230 900005 ID_564510 230 1 | Line | Cumberland - Delco 230kV | [19 empty] | 150.22 | 99.39 | 95.88 | 138.72 | 133.98 | [21 empty] | 147.92 | 95.85 | 92.44 | 135.77 | 130.69 | [20 empty] | 157.14 | 102.89 | 99.46 | 143.67 | 138.57 | [21 empty] | 96.62 | 96.62 |  |  |  |  | 96.6 | [19 empty] | 100.19 | 100.19 |  |  | 90.71 |  | 100.17 | [23 empty] | 101.16 | 101.12 |  |  | 92.48 |  | 101.09 | 0 | 157.14 | 3 | 3 | 4 | 0 | 3 | 3 | 3 | 6 | 7 | 3 | 0 | NO |  |  |  | 7591.58 | Yes | 8 | No
304582,305033,1 | 230 | 304582 DELCO230 TT 230 305033 E4-KELLY 230 1 | Line | Cumberland - Delco 230kV | [19 empty] | 143.97 | 94.49 | 90.79 | 133.14 | 128.69 | [21 empty] | 141.69 | 90.93 |  | 130.21 | 125.48 | [20 empty] | 150.62 | 98.01 | 94.46 | 137.92 | 133.17 | [21 empty] | 101.3 | 101.31 |  |  | 93.12 |  | 101.29 | [19 empty] | 104.92 | 104.92 |  |  | 95.37 | 91.29 | 104.9 | [23 empty] | 105.9 | 105.86 |  |  | 97.16 | 93.47 | 105.83 | 0 | 150.62 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 3 | 0 | NO |  |  |  | 7551.58 | Yes | 8 | No
305033,305390,1 | 230 | 305033 E4-KELLY 230 305390 ROWANSOL-TAP 230 1 | Line | Cumberland - Delco 230kV | [19 empty] | 139.05 |  |  | 128.31 | 123.92 | [21 empty] | 136.77 |  |  | 125.38 | 120.72 | [20 empty] | 145.57 | 93.46 |  | 133.01 | 128.33 | [21 empty] | 96.62 | 96.63 |  |  |  |  | 96.61 | [19 empty] | 100.19 | 100.2 |  |  | 90.71 |  | 100.18 | [23 empty] | 101.16 | 101.12 |  |  | 92.48 |  | 101.1 | 0 | 145.57 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 6 | 6 | 3 | 0 | NO |  |  |  | 7551.58 | Yes | 8 | No
305830,900005,1 | 230 | 305830 BAYTRESOLTAP 230 900005 ID_564510 230 1 | Line | Cumberland - Delco 230kV | 97.88 |  |  | 91.95 | [15 empty] | 157.66 | 105.85 | 102.62 | 145.69 | 140.74 |  | 95.97 | [19 empty] | 155.36 | 102.43 | 99.25 | 142.73 | 137.4 | 95.49 | [19 empty] | 164.83 | 109.35 | 106.04 | 150.78 | 145.42 | [21 empty] | 96.61 | 96.61 |  |  |  |  | 96.59 | [19 empty] | 100.18 | 100.18 |  |  | 90.7 |  | 100.16 | [23 empty] | 101.15 | 101.11 |  |  | 92.46 |  | 101.08 | 0 | 164.83 | 5 | 4 | 5 | 0 | 3 | 3 | 5 | 7 | 8 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304387,304390,2 | 230 | 304387 FAY 230 TT 230 304390 CUMBLND230TT 230 2 | Line | Cumberland - Fayetteville 230kV South | [19 empty] | 107.1 |  |  | 104.15 | 96.33 | [21 empty] | 103.97 |  |  | 100.6 | 92.46 | [20 empty] | 104.44 |  |  | 101.08 | 93.13 | [84 empty] | 0 | 107.1 | 2 | 2 | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304600,305330,1 | 230 | 304600 WHITEVL230TT 230 305330 BLADENSOLTAP 230 1 | Line | Cumberland - Whiteville 230kV | [19 empty] | 110.34 |  |  | 109.9 | 98.34 | [21 empty] | 100.53 |  |  | 99.68 | [21 empty] | 98.35 |  |  | 97.07 | [85 empty] | 0 | 110.34 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 0 | NO |  |  |  | 6414.37 | Yes | 7 | No
305034,305035,1 | 230 | 305034 E4-POWELL 230 305035 E4-TARHELL 230 1 | Line | Cumberland - Whiteville 230kV |  |  |  | 90.63 | [15 empty] | 108.19 |  |  | 107.65 | 96.58 | [21 empty] | 98.85 |  |  | 98.07 | [21 empty] | 96.39 |  |  | 95.26 | [85 empty] | 0 | 108.19 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | NO |  |  |  | 6454.37 | Yes | 7 | No
304390,305035,1 | 230 | 304390 CUMBLND230TT 230 305035 E4-TARHELL 230 1 | Line | Cumberland - Whiteville 230kV | [19 empty] | 101.01 |  |  | 100.34 | [22 empty] | 91.71 |  |  | 90.71 | [110 empty] | 0 | 101.01 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304580,304581,1 | 115 | 304580 E1WHITVLTAP 115 304581 WHITEVL115TT 115 1 | Line | Delco - Whiteville 115kV | [19 empty] | 96.3 | [25 empty] | 100.69 | [24 empty] | 107.2 |  |  | 93.6 | 95.86 | [84 empty] | 0 | 107.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | NO |  |  |  | 6184.79 | No | 7 | No
304582,304587,1 | 230 | 304582 DELCO230 TT 230 304587 DELCO115W TT 115 1 | Substation | Delco 230kV | [19 empty] | 168.98 | 116.73 | 121.29 | 156.32 | 156.84 |  | 90.97 | [19 empty] | 171.86 | 118.94 | 123.94 | 158.77 | 158.96 | 98.01 |  |  |  | 92.29 | [10 empty] | 91.48 |  |  |  |  | 182.26 | 129.2 | 133.64 | 169.49 | 169.86 | [21 empty] | 160.01 | 160.13 | 107.99 | 112.88 | 148.46 | 149.62 | 160.11 | [19 empty] | 164.84 | 164.96 | 111.62 | 116.47 | 151.91 | 152.67 | 164.94 | [23 empty] | 167.99 | 168.1 | 115.49 | 120.34 | 156.14 | 157.08 | 168.08 | 0 | 182.26 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  | 5992.43 | Yes | 6 | No
304582,304583,2 | 230 | 304582 DELCO230 TT 230 304583 DELCO115E TT 115 2 | Substation | Delco 230kV | [19 empty] | 145.26 | 99.7 | 103.64 | 134.26 | 134.82 | [21 empty] | 147.76 | 101.67 | 105.58 | 136.55 | 136.64 | [20 empty] | 156.84 | 110.66 | 114.43 | 145.86 | 146.17 | [21 empty] | 137.48 | 137.59 | 92.28 | 96.44 | 127.4 | 128.41 | 137.57 | [19 empty] | 141.73 | 141.83 | 95.41 | 99.53 | 130.56 | 131.15 | 141.81 | [23 empty] | 144.53 | 144.63 | 98.79 | 102.91 | 134.2 | 135.04 | 144.61 | 0 | 156.84 | 4 | 5 | 5 | 5 | 5 | 6 | 9 | 10 | 11 | 3 | 0 | NO |  |  |  | 5865.72 | Yes | 6 | No
304583,304587,Z1 | 115 | 304583 DELCO115E TT 115 304587 DELCO115W TT 115 Z1 | Substation | Delco 230kV | [19 empty] | 91.6 | [25 empty] | 92.79 | [24 empty] | 96.75 |  |  | 90.4 | [85 empty] | 0 | 96.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304187,304193,1 | 230 | 304187 PA-SMTHFLD2 230 304193 FOUR OAKS 230 1 | Line | Erwin - Selma 230kV | 93.85 |  |  | 93.96 | [21 empty] | 90.61 | [24 empty] | 93.56 |  |  | 91.95 | [11 empty] | 90.89 |  |  |  |  | 120.93 | 93.76 | 94.18 | 115.29 | 105.71 | [84 empty] | 0 | 120.93 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | NO |  |  |  | 6476.25 | Yes | 7 | No
304193,304259,1 | 230 | 304193 FOUR OAKS 230 304259 CLV MAT TAP 230 1 | Line | Erwin - Selma 230kV | 92.36 |  |  | 92.32 | [46 empty] | 92.05 |  |  | 90.28 | [16 empty] | 116.97 |  | 90.28 | 111.25 | 101.74 | [84 empty] | 0 | 116.97 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | NO |  |  |  | 6476.25 | Yes | 7 | No
304194,304217,1 | 230 | 304194 BENSON 230 304217 BENPGI TAP 230 1 | Line | Erwin - Selma 230kV | [70 empty] | 102.93 |  |  | 97.21 | [85 empty] | 0 | 102.93 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | NO |  |  |  | 6476.25 | Yes | 7 | No
304187,304192,1 | 230 | 304187 PA-SMTHFLD2 230 304192 SELMA 230 TT 230 1 | Line | Erwin - Selma 230kV | 94.78 |  |  | 94.9 | [21 empty] | 91.56 |  |  | 90.03 | [21 empty] | 94.5 |  |  | 92.91 | [11 empty] | 92.29 |  |  | 91 |  | 122.21 | 95 | 95.42 | 116.57 | 106.97 | [84 empty] | 0 | 122.21 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304194,304259,1 | 230 | 304194 BENSON 230 304259 CLV MAT TAP 230 1 | Line | Erwin - Selma 230kV | [70 empty] | 109.19 |  |  | 103.55 | 94.18 | [84 empty] | 0 | 109.19 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304196,304217,1 | 230 | 304196 ERWIN230 TT 230 304217 BENPGI TAP 230 1 | Line | Erwin - Selma 230kV | [70 empty] | 100.47 |  |  | 94.71 | [85 empty] | 0 | 100.47 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | NO |  |  |  |  | Yes | 0 | No
304480,304481,1 | 115 | 304480 KINSDUP115TT 115 304481 PA-AYDEN 115 1 | Line | Goldsboro SS - Kinston DuPont 115kV | 93.49 |  |  | 91.33 | [15 empty] | 106.1 | 93.97 | 93.95 | 102.06 | 99.06 |  | 90.24 | [19 empty] | 105.34 | 92.71 | 92.68 | 100.74 | 97.66 | [20 empty] | 94.22 |  |  | 90.59 | [48 empty] | 90.55 | 90.51 |  |  |  |  | 90.51 | [30 empty] | 0 | 106.1 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | NO |  |  |  | 3159.15 | Yes | 4 | No
304459,304481,1 | 115 | 304459 GRIFTON 115 304481 PA-AYDEN 115 1 | Line | Goldsboro SS - Kinston DuPont 115kV | [19 empty] | 95.1 |  |  | 91.11 | [22 empty] | 94.25 | [113 empty] | 0 | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304525,305065,1 | 115 | 304525 JACKSN115ETT 115 305065 E9-GUMBRNCH 115 1 | Line | Jacksonville - Wommack 115kV | [19 empty] | 129.09 | 104.3 | 104.72 | 137.56 | 131.06 | [21 empty] | 137.09 | 110.16 | 110.65 | 144.17 | 137.18 | [20 empty] | 108.34 |  |  | 104.13 | 113.53 | [21 empty] | 0 | 0 |  |  |  |  | 0 | [56 empty] | 0 | 144.17 | 5 | 5 | 3 | 0 | 0 | 0 | 5 | 5 | 3 | 3 | 0 | NO |  |  | 138.1 | 2943.64 | Yes | 4 | No
305065,305079,1 | 115 | 305065 E9-GUMBRNCH 115 305079 E9-FRANTOWN 115 1 | Line | Jacksonville - Wommack 115kV | [19 empty] | 118.35 | 94.02 | 94.44 | 126.76 | 120.41 | [21 empty] | 126 | 99.4 | 99.89 | 133.01 | 126.17 | [20 empty] | 97.69 |  |  | 93.72 | 103.1 | [84 empty] | 0 | 133.01 | 3 | 3 | 1 | 0 | 0 | 0 | 3 | 3 | 1 | 3 | 0 | NO |  |  | 150.04 | 2913.64 | Yes | 4 | No
305062,305080,1 | 115 | 305062 E9-EAGLE NST 115 305080 E9-ELMGROVE 115 1 | Line | Jacksonville - Wommack 115kV | [19 empty] | 115.18 |  | 90.37 | 122.93 | 116.37 | [21 empty] | 122.9 | 95.39 | 95.85 | 129.18 | 122.12 | [20 empty] | 94.41 |  |  | 0 | 98.99 | [84 empty] | 0 | 129.18 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | NO |  |  |  | 2933.64 | Yes | 3 | No
304507,305072,1 | 115 | 304507 WOMACKE115TT 115 305072 E9-PLEASANT 115 1 | Line | Jacksonville - Wommack 115kV | 98.46 |  |  | 95.56 | 90.71 | [14 empty] | 137.01 | 108.9 | 109.26 | 142.82 | 135.38 | [21 empty] | 116.28 |  |  | 122.62 | 115.68 | [20 empty] | 116.5 |  |  | 109.67 | 117.72 | [47 empty] | 0 | 0 |  |  |  |  | 0 | [30 empty] | 0 | 142.82 | 5 | 3 | 3 | 0 | 0 | 0 | 5 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305062,305079,1 | 115 | 305062 E9-EAGLE NST 115 305079 E9-FRANTOWN 115 1 | Line | Jacksonville - Wommack 115kV | [19 empty] | 127.05 | 101.26 | 101.66 | 134.78 | 128.02 | [21 empty] | 135.37 | 107.43 | 107.89 | 141.67 | 134.41 | [20 empty] | 106.25 |  |  | 101.33 | 110.36 | [84 empty] | 0 | 141.67 | 5 | 5 | 3 | 0 | 0 | 0 | 5 | 5 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305072,305080,1 | 115 | 305072 E9-PLEASANT 115 305080 E9-ELMGROVE 115 1 | Line | Jacksonville - Wommack 115kV | [19 empty] | 110.37 |  |  | 118.19 | 111.72 | [21 empty] | 117.82 | 90.55 | 91.02 | 124.15 | 117.18 | [20 empty] | 0 |  |  | 0 | 94.45 | [84 empty] | 0 | 124.15 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | NO |  |  |  |  | Yes | 0 | No
304280,305151,1 | 115 | 304280 BEULAVILLE 115 305151 E17-BEULAVIL 115 1 | Line | Lee - Wallace 115kV | [19 empty] | 126.16 | 94.14 | 94.47 | 122.44 | 116.65 | [21 empty] | 134.4 | 98.47 | 98.74 | 128.68 | 120.76 | [20 empty] | 105.37 |  |  | 101.17 | 95.57 | [84 empty] | 0 | 134.4 | 3 | 3 | 2 | 0 | 0 | 0 | 3 | 3 | 2 | 3 | 0 | NO |  |  |  | 2749.99 | Yes | 3 | No
305151,305161,1 | 115 | 305151 E17-BEULAVIL 115 305161 E17-TAPPFARM 115 1 | Line | Lee - Wallace 115kV | [19 empty] | 123.76 | 91.88 | 92.22 | 120.08 | 114.32 | [21 empty] | 131.89 | 95.99 | 96.26 | 126.21 | 118.24 | [20 empty] | 103 |  |  | 98.85 | 93.32 | [84 empty] | 0 | 131.89 | 3 | 3 | 1 | 0 | 0 | 0 | 3 | 3 | 1 | 3 | 0 | NO |  |  |  | 2670.04 | Yes | 3 | No
304280,304517,1 | 115 | 304280 BEULAVILLE 115 304517 WALLACE115TT 115 1 | Line | Lee - Wallace 115kV | [19 empty] | 124.25 | 92.7 | 93.03 | 120.89 | 115.22 | [21 empty] | 132.42 | 96.96 | 97.24 | 127.12 | 119.28 | [20 empty] | 103.51 |  |  | 99.66 | 94.18 | [21 empty] | 106.17 | 106.04 |  |  | 103.23 | 97.5 | 106.06 | [49 empty] | 93.57 | 93.44 |  |  | 90.91 |  | 93.48 | 0 | 132.42 | 3 | 3 | 1 | 4 | 0 | 0 | 7 | 3 | 1 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305158,305161,1 | 115 | 305158 E17-KORNEGAY 115 305161 E17-TAPPFARM 115 1 | Line | Lee - Wallace 115kV | [19 empty] | 113.49 |  |  | 110.04 | 104.47 | [21 empty] | 121.01 |  |  | 115.51 | 107.25 | [20 empty] | 92.91 | [88 empty] | 0 | 121.01 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | NO |  |  |  |  | Yes | 0 | No
304273,305158,1 | 115 | 304273 KORNEGAY SUB 115 305158 E17-KORNEGAY 115 1 | Line | Lee - Wallace 115kV | [19 empty] | 113.25 |  |  | 109.8 | 104.23 | [21 empty] | 120.77 |  |  | 115.27 | 107.01 | [20 empty] | 92.67 | [88 empty] | 0 | 120.77 | 3 | 3 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 2 | 0 | NO |  |  |  |  | Yes | 0 | No
304031,305154,1 | 115 | 304031 LEESEP115ETT 115 305154 E17-FREMONT 115 1 | Line | Lee Plant - Black Creek SS 115kV West | [70 empty] | 100.5 | [74 empty] | 92.32 | 92.21 |  |  |  |  | 92.27 | 94.6 | 94.51 |  |  |  |  | 94.53 | 0 | 100.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | NO |  |  |  | 1247.06 | Yes | 2 | No
304238,305154,1 | 115 | 304238 BLACKCREEKTT 115 305154 E17-FREMONT 115 1 | Line | Lee Plant - Black Creek SS 115kV West | [70 empty] | 97.07 | [81 empty] | 90.8 | 90.71 |  |  |  |  | 90.73 | 0 | 97.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304581,304597,1 | 115 | 304581 WHITEVL115TT 115 304597 WHITEVILTAP 115 1 | Line | Marion - Whiteville 115kV | [70 empty] | 97.55 | [88 empty] | 0 | 97.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304039,304554,1 | 230 | 304039 SUTTON230 TT 230 304554 WILM N&O TAP 230 1 | Line | Sutton Plant - Castle Hayne 230kV | [19 empty] | 109.16 | 106.86 | 108.5 | 104.31 | 104.08 | [21 empty] | 110.28 | 107.33 | 108.94 | 104.88 | 104.57 | [20 empty] | 113.63 | 110.54 | 112.24 | 108.14 | 107.78 | [84 empty] | 0 | 113.63 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 5 | 3 | 0 | NO |  |  |  | 2725.04 | Yes | 3 | No
304552,304577,1 | 230 | 304552 WILM EAST 230 304577 MURRAYVILLE 230 1 | Line | Sutton Plant - Castle Hayne 230kV | [19 empty] | 95.36 | 93.2 | 94.8 | 90.58 | 90.35 | [21 empty] | 96.44 | 93.65 | 95.27 | 91.14 | 90.84 | [20 empty] | 99.68 | 96.85 | 98.51 | 94.34 | 94.02 | [21 empty] | 91.61 | 91.64 | 90.49 | 92 |  |  | 91.64 | [19 empty] | 92.26 | 92.29 | 90.62 | 92.1 |  |  | 92.28 | [23 empty] | 93.66 | 93.68 | 92.44 | 93.9 |  |  | 93.68 | 0 | 99.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  | 2725.04 | Below 100% | 3 | No
304552,304554,1 | 230 | 304552 WILM EAST 230 304554 WILM N&O TAP 230 1 | Line | Sutton Plant - Castle Hayne 230kV | [19 empty] | 102.39 | 100.15 | 101.77 | 97.57 | 97.34 | [21 empty] | 103.5 | 100.61 | 102.22 | 98.13 | 97.83 | [20 empty] | 106.8 | 103.82 | 105.49 | 101.37 | 101.03 | [21 empty] | 97.33 | 97.36 | 96.17 | 97.72 | 93.21 | 93.2 | 97.36 | [19 empty] | 97.99 | 98.02 | 96.3 | 97.81 | 93.43 | 93.23 | 98.02 | [23 empty] | 99.4 | 99.43 | 98.12 | 99.6 | 95.15 | 95.16 | 99.42 | 0 | 106.8 | 3 | 3 | 5 | 0 | 0 | 0 | 3 | 3 | 5 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304550,304577,1 | 230 | 304550 CASTLEH230TT 230 304577 MURRAYVILLE 230 1 | Line | Sutton Plant - Castle Hayne 230kV | [19 empty] | 90.88 |  | 90.37 | [23 empty] | 91.93 |  | 90.84 | [22 empty] | 95.12 | 92.42 | 94.05 | [86 empty] | 0 | 95.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304039,304605,1 | 230 | 304039 SUTTON230 TT 230 304605 RESILIENCE 230 1 | Line | Sutton Plant - Delco 230kV | [19 empty] | 143.66 | 123.37 | 131.02 | 133.55 | 133.07 | [21 empty] | 144.42 | 123.93 | 131.03 | 133.78 | 133.25 | [20 empty] | 153.37 | 132.03 | 140.08 | 143.23 | 142.52 | [21 empty] | 97.89 | 97.95 |  |  | 91.17 | 90.98 | 97.93 | [19 empty] | 101.05 | 101.11 |  | 91.98 | 93.76 | 93.22 | 101.09 | [23 empty] | 102.87 | 102.93 |  | 94.13 | 95.89 | 95.8 | 102.91 | 0 | 153.37 | 5 | 5 | 5 | 0 | 3 | 3 | 5 | 8 | 8 | 3 | 0 | NO |  |  |  | 7333.01 | Yes | 8 | No
304582,304605,1 | 230 | 304582 DELCO230 TT 230 304605 RESILIENCE 230 1 | Line | Sutton Plant - Delco 230kV | [19 empty] | 111.66 | 92.61 | 100.14 | 102.08 | 101.76 | [21 empty] | 112.45 | 93.18 | 100.25 | 102.34 | 101.87 | [20 empty] | 121.03 | 101.22 | 108.96 | 111.33 | 110.8 | [84 empty] | 0 | 121.03 | 4 | 4 | 5 | 0 | 0 | 0 | 4 | 4 | 5 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304516,304578,1 | 230 | 304516 WILM BASF 230 304578 WILMCTFSHCR 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 241.43 | 220.22 | 227.77 | 229.55 | 228.29 | [21 empty] | 243.05 | 220.93 | 229.06 | 230.08 | 227.12 | [20 empty] | 249.07 | 232.41 | 241 | 235.49 | 232.89 | [21 empty] | 197.02 | 197.06 | 180.66 | 189.65 | 188.13 | 186.25 | 197.05 | [19 empty] | 199.6 | 199.64 | 183.6 | 192.23 | 189.37 | 186.94 | 199.62 | [23 empty] | 200.85 | 200.89 | 187.74 | 196.92 | 191.2 | 189.19 | 200.88 | 0 | 249.07 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  | 7333.01 | Yes | 8 | No
305470,305880,1 | 230 | 305470 WILARDSOLTAP 230 305880 CROOKDSOLTAP 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 147.89 | 113.9 | 114.44 | 144.24 | 137.88 | [21 empty] | 145.73 | 110.97 | 111.53 | 141.03 | 134.84 | [20 empty] | 133.37 | 102.33 | 103.22 | 130.51 | 124.01 | [21 empty] | 120.89 | 120.78 | 92.15 | 93.13 | 118.41 | 112.82 | 120.8 | [19 empty] | 117.72 | 117.6 |  |  | 114.53 | 108.74 | 117.62 | [23 empty] | 113.67 | 113.55 |  |  | 111.21 | 105.87 | 113.58 | 0 | 147.89 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 3 | 0 | NO |  |  |  | 3427.54 | Yes | 4 | No
304516,305995,1 | 230 | 304516 WILM BASF 230 305995 6SUTNORTH230 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 286.48 | 261.38 | 270.31 | 272.43 | 270.95 | [21 empty] | 288.39 | 262.22 | 271.82 | 273.06 | 269.55 | [20 empty] | 295.52 | 275.78 | 285.94 | 279.46 | 276.38 | [21 empty] | 221.58 | 221.62 | 203.23 | 213.3 | 211.62 | 209.52 | 221.61 | [19 empty] | 224.47 | 224.51 | 206.53 | 216.19 | 213.02 | 210.28 | 224.5 | [23 empty] | 225.88 | 225.92 | 211.16 | 221.45 | 215.07 | 212.81 | 225.9 | 0 | 295.52 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304039,304520,1 | 230 | 304039 SUTTON230 TT 230 304520 WILM INVISTA 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 280.15 | 255.23 | 264.13 | 266.16 | 264.65 | [21 empty] | 282.04 | 256.08 | 265.66 | 266.76 | 263.31 | [20 empty] | 289.08 | 269.63 | 279.73 | 273.11 | 270.06 | [21 empty] | 216.46 | 216.51 | 198.27 | 208.3 | 206.54 | 204.45 | 216.5 | [19 empty] | 219.34 | 219.38 | 201.56 | 211.18 | 207.92 | 205.22 | 219.36 | [23 empty] | 220.72 | 220.77 | 206.18 | 216.42 | 209.96 | 207.72 | 220.75 | 0 | 289.08 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304534,304578,1 | 230 | 304534 WILM PRAX 230 304578 WILMCTFSHCR 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 240.12 | 218.91 | 226.47 | 228.24 | 226.98 | [21 empty] | 241.74 | 219.63 | 227.75 | 228.77 | 225.81 | [20 empty] | 247.76 | 231.11 | 239.69 | 234.18 | 231.58 | [21 empty] | 195.91 | 195.95 | 179.55 | 188.54 | 187.02 | 185.14 | 195.93 | [19 empty] | 198.49 | 198.52 | 182.5 | 191.12 | 188.26 | 185.83 | 198.51 | [23 empty] | 199.74 | 199.78 | 186.63 | 195.81 | 190.09 | 188.08 | 199.76 | 0 | 247.76 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304520,304534,1 | 230 | 304520 WILM INVISTA 230 304534 WILM PRAX 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 238.7 | 217.54 | 225.09 | 226.84 | 225.57 | [21 empty] | 240.31 | 218.26 | 226.38 | 227.36 | 224.42 | [20 empty] | 246.31 | 229.74 | 238.31 | 232.75 | 230.16 | [21 empty] | 194.69 | 194.73 | 178.39 | 187.36 | 185.81 | 183.94 | 194.72 | [19 empty] | 197.27 | 197.31 | 181.33 | 189.94 | 187.05 | 184.63 | 197.29 | [23 empty] | 198.51 | 198.55 | 185.46 | 194.62 | 188.88 | 186.87 | 198.54 | 0 | 246.31 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304515,305880,1 | 230 | 304515 WALLACE230TT 230 305880 CROOKDSOLTAP 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 124.5 | 96.83 | 97.26 | 121.29 | 116.08 | [21 empty] | 122.81 | 94.47 | 94.91 | 118.73 | 113.63 | [20 empty] | 112.85 |  |  | 110.28 | 104.95 | [21 empty] | 92.47 | 92.38 |  |  | 90.57 |  | 92.4 | [19 empty] | 90.05 | [36 empty] | 0 | 124.5 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305470,305995,1 | 230 | 305470 WILARDSOLTAP 230 305995 6SUTNORTH230 230 1 | Line | Sutton Plant - Wallace 230kV | [19 empty] | 103.77 |  |  | 102.36 | 97.02 | [21 empty] | 101.1 |  |  | 98.9 | 93.87 | [46 empty] | 94.61 | 94.49 |  |  | 93.25 |  | 94.51 | [19 empty] | 91.48 | 91.37 |  |  |  |  | 91.39 | [30 empty] | 0 | 103.77 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 2 | 0 | NO |  |  |  |  | Yes | 0 | No
304515,304517,1 | 230 | 304515 WALLACE230TT 230 304517 WALLACE115TT 115 1 | Substation | Wallace 230kV | [19 empty] | 148.81 | 129.63 | 130.41 | 144.7 | 141.4 | [21 empty] | 154.92 | 131.67 | 132.44 | 149.09 | 143.97 | [20 empty] | 138.54 | 116.55 | 118.25 | 133.77 | 128.52 | [16 empty] | 90.67 |  |  |  |  | 147.55 | 147.49 | 129.75 | 130.6 | 143.5 | 139.8 | 147.49 | [19 empty] | 138.07 | 138.01 | 119.14 | 120.17 | 133.81 | 129.92 | 138.01 | [23 empty] | 140.75 | 140.69 | 126.21 | 127.42 | 136.73 | 132.89 | 140.71 | 0 | 154.92 | 5 | 5 | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 3 | 0 | NO |  |  |  | 2790.04 | Yes | 3 | No
304570,304571,1 | 115 | 304570 CLARKTON 115 304571 ELIZTOWN TAP 115 1 | Line | Weatherspoon Plant - Delco 115kV | [19 empty] | 131.44 |  |  | 117.02 | 116.89 | [21 empty] | 134.59 |  |  | 119.48 | 118.68 | [20 empty] | 146.72 | 93.36 | 91.73 | 130.87 | 130.12 | [84 empty] | 0 | 146.72 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  | 3086.79 | Yes | 4 | No
304571,304574,1 | 115 | 304571 ELIZTOWN TAP 115 304574 BLADENBORO 115 1 | Line | Weatherspoon Plant - Delco 115kV | [19 empty] | 123.46 |  |  | 109.02 | 108.95 | [21 empty] | 126.56 |  |  | 111.46 | 110.72 | [20 empty] | 138.48 |  |  | 122.78 | 122.08 | [84 empty] | 0 | 138.48 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  | 3086.79 | Yes | 4 | No
304047,304574,1 | 115 | 304047 WSPOON115 TT 115 304574 BLADENBORO 115 1 | Line | Weatherspoon Plant - Delco 115kV | 95.95 | [18 empty] | 138.59 |  |  | 122.34 | 122.19 |  | 90.7 | [19 empty] | 142.05 |  |  | 125.04 | 124.14 | 93.35 | [19 empty] | 155.33 | 96.32 | 94.48 | 137.64 | 136.8 | [84 empty] | 0 | 155.33 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304576,304583,1 | 115 | 304576 KINGS BLUFF 115 304583 DELCO115E TT 115 1 | Line | Weatherspoon Plant - Delco 115kV | [19 empty] | 133.29 |  |  | 119.01 | 118.92 | [21 empty] | 136.44 |  |  | 121.49 | 120.73 | [20 empty] | 148.61 | 95.35 | 93.72 | 132.88 | 132.17 | [84 empty] | 0 | 148.61 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
304570,304576,1 | 115 | 304570 CLARKTON 115 304576 KINGS BLUFF 115 1 | Line | Weatherspoon Plant - Delco 115kV | [19 empty] | 131.79 |  |  | 117.53 | 117.45 | [21 empty] | 134.94 |  |  | 120 | 119.26 | [20 empty] | 147.06 | 93.91 | 92.28 | 131.38 | 130.67 | [84 empty] | 0 | 147.06 | 3 | 3 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 0 | NO |  |  |  |  | Yes | 0 | No
305138,305380,1 | 230 | 305138 E15-LBRTYPT 230 305380 COLINSOL-TAP 230 1 | Line | Weatherspoon Plant - Fayetteville 230kV | [22 empty] | 97.35 | [136 empty] | 0 | 97.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
304047,305099,1 | 115 | 304047 WSPOON115 TT 115 305099 E10-WESTLUMB 115 1 | Line | Weatherspoon Plant - Libbey Owens Ford 115kV | [19 empty] | 90.81 |  |  | 90.96 | [22 empty] | 90.28 | [24 empty] | 98.62 |  |  | 91.49 | 92.76 | [14 empty] | 93.15 | 93.14 | 94.15 | 93.91 | 93.42 | 93.05 | 93.14 | [19 empty] | 93.34 | 93.32 | 94.1 | 93.78 | 93.76 | 93.17 | 93.32 | [23 empty] | 93.68 | 93.67 | 93.7 | 93.57 | 93.81 | 93.36 | 93.67 | [7 empty] | 0 | 98.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  | 102.5 | Below 100% | 1 | No
304047,304432,1 | 115 | 304047 WSPOON115 TT 115 304432 PA-LUMB#2 115 1 | Line | Weatherspoon Plant - Raeford 115kV | [19 empty] | 93.3 |  |  | 98.64 | [136 empty] | 0 | 98.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  | 144.4 |  | Below 100% | 1 | No
Note on GA5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?

## BuckCC
Buck CC Cluster
[6 empty] | Exclusion Criteria |  |  | Exclusion Criteria | Scenario 1 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 2 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 3 - Summer Cases - Max Branch Loading [%] |  |  |  |  | Scenario 1 - Winter - Max Branch Loading [%] |  |  |  | Scenario 2 - Winter - Max Branch Loading [%] |  |  |  | Scenario 3 - Winter - Max Branch Loading [%] |  |  |  |  | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
Duke Energy Carolinas Overloads | [9 empty] | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base - CSM | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Base | 110 | 90 | OFW | Max Loading [%] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | From Bus | From Bus Name | To Bus | To Bus Name | Circuit | Voltage | Line or Substation | Branch Name | Branch Type | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_WP_OFW | Grand Total | # of Scenarios (3) | # of Base Cases (9) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project
306560,306869,1 | 306560 | BUCK S34 | 306869 | ENRG U35 | 1 | 100 | Line | ARCADIA BL | 100 kV Line | 0 | 0 | 0 | 0 | 0 | 0 | 99.9 | 0 | 95.5 | 0 | 111.2 | 93.7 | 0 | 91.6 | 0 | 95.1 | 98 | 0 | 0 | 120.9 | 103.2 | 111.4 | 112.4 | 110.8 | 117.2 | 102.5 | 109.6 | 120.9 | 2 | 3 | NO |  |  |  | 2828.4 | Yes | 3 | No
306738,306869,1 | 306738 | ENRG U40 | 306869 | ENRG U35 | 1 | 100 | Line | ARCADIA BL | 100 kV Line | [5 empty] | 0 | 105.1 | 0 | 102.7 | 0 | 126.9 | 94.9 | 0 | 96.5 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.9 | 2 | 2 | NO |  |  |  | 1469.2 | Yes | 2 | No
306560,308574,1 | 306560 | BUCK S34 | 308574 | ENRG U35TW | 1 | 100 | Line | ARCADIA WH | 100 kV Line | 0 | 0 | 0 | 0 | 0 | 0 | 100.4 | 0 | 95.5 | 0 | 102.2 | 93.9 | 0 | 91.6 | 0 | 0 | 97.4 | 0 | 0 | 119.8 | 102.8 | 110.5 | 111.6 | 109.8 | 116.2 | 101.2 | 108.7 | 119.8 | 2 | 4 | NO |  |  |  | 2924 | Yes | 3 | No
308573,308574,1 | 308573 | ENRG U40TW | 308574 | ENRG U35TW | 1 | 100 | Line | ARCADIA WH | 100 kV Line | [5 empty] | 0 | 112.9 | 0 | 109.3 | 102.4 | 134.6 | 103 | 95.2 | 103.4 | 96.6 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6 | 2 | 3 | NO |  |  |  | 2863.4 | Yes | 3 | No
308573,309899,1 | 308573 | ENRG U40TW | 309899 | LEXCTY3 | 1 | 100 | Line | ARCADIA WH | 100 kV Line | [10 empty] | 99.9 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 99.9 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306687,309963,1 | 306687 | WINECOFF | 309963 | CONCORD5 | 1 | 100 | Line | BUCK BL | 100 kV Line | [5 empty] | 0 | 0 | 98.8 | 0 | 99.1 | 132.1 | 94.5 | 95.5 | 97.3 | 99.3 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.1 | 1 | 1 | NO |  |  |  | 2836.6 | No | 3 | No
306275,306560,1 | 306275 | DUNNMTNT | 306560 | BUCK S34 | 1 | 100 | Line | BUCK BL | 100 kV Line | [5 empty] | 0 | 0 | 100.5 | 0 | 98.6 | 113.1 | 93.6 | 99 | 91.6 | 98.2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1 | 2 | 1 | YES |  |  |  | 1438.6 | Yes | 3 | No
306275,308379,1 | 306275 | DUNNMTNT | 308379 | FAITH BL | 1 | 100 | Line | BUCK BL | 100 kV Line | [5 empty] | 0 | 0 | 100.6 | 0 | 98.6 | 113.1 | 93.6 | 99 | 91.6 | 98.2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1 | 2 | 1 | YES |  |  |  | 1438.6 | Yes | 3 | No
306558,308379,1 | 306558 | BRNTLY T | 308379 | FAITH BL | 1 | 100 | Line | BUCK BL | 100 kV Line | [10 empty] | 108 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 108 | 1 | 1 | NO |  |  |  |  | No | 0 | No
306558,309963,1 | 306558 | BRNTLY T | 309963 | CONCORD5 | 1 | 100 | Line | BUCK BL | 100 kV Line | [10 empty] | 107.9 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 107.9 | 1 | 1 | NO |  |  |  |  | No | 0 | No
306560,306561,1 | 306560 | BUCK S34 | 306561 | BUCK TIE | 1 | 100 | Line | BUCK TIE - BUCK STEAM SEC 4 BUS RED | 100 kV Line | 0 | 0 | 95.5 | 0 | 0 | [10 empty] | 130.4 | 140.1 | 124.3 | 136.1 | [8 empty] | 140.1 | 1 | 1 | YES |  |  | 106.5 | 2571.8 | Yes | 5 | No
306560,306561,2 | 306560 | BUCK S34 | 306561 | BUCK TIE | 2 | 100 | Line | BUCK TIE - BUCK STEAM SEC 4 BUS YEL | 100 kV Line | 0 | 0 | 95.5 | 0 | 0 | [10 empty] | 130.7 | 140.1 | 124.3 | 136.1 | [8 empty] | 140.1 | 1 | 1 | YES |  |  | 106.5 | 2571.8 | Yes | 5 | No
306563,308380,1 | 306563 | BARRIER RT | 308380 | BRANT WH | 1 | 100 | Line | BUCK WH | 100 kV Line | [5 empty] | 0 | 124.7 | 140.7 | 125.4 | 140.2 | 147.1 | 133.3 | 138.7 | 131.2 | 139 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1 | 2 | 3 | YES |  |  |  | 1446.2 | Yes | 3 | No
306687,308380,1 | 306687 | WINECOFF | 308380 | BRANT WH | 1 | 100 | Line | BUCK WH | 100 kV Line | [5 empty] | 0 | 113.6 | 124.9 | 122.5 | 129 | 154.9 | 122 | 122.4 | 128.4 | 128.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.9 | 2 | 3 | NO |  |  |  | 1481.2 | Yes | 2 | No
306560,306586,1 | 306560 | BUCK S34 | 306586 | FAITH | 1 | 100 | Line | BUCK WH | 100 kV Line | [10 empty] | 97.8 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 97.8 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306563,306586,1 | 306563 | BARRIER RT | 306586 | FAITH | 1 | 100 | Line | BUCK WH | 100 kV Line | [10 empty] | 97.7 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 97.7 | 0 | 0 | NO |  |  |  |  | Below 100% | 0 | No
306681,306685,1 | 306681 | WESTFORK | 306685 | WILDCAT | 1 | 100 | Line | CABARRUS BL | 100 kV Line | 128.7 | 151.2 | 178 | 128.9 | 152.9 | 128.7 | 152.7 | 178.9 | 129.9 | 152.7 | 130.3 | 153.6 | 180 | 130 | 153.5 | 0 | 106 | 0 | 0 | 0 | 106.4 | 0 | 0 | 94 | 106.2 | 0 | 94 | 180 | 3 | 6 | YES | 135.7 |  |  |  | Yes | 2 | Conceptual
306681,308893,1 | 306681 | WESTFORK | 308893 | WILDCATT WH | 1 | 100 | Line | CABARRUS WH | 100 kV Line | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 109.6 | 0 | 0 | 0 | 94.6 | 110 | 0 | 94.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 3 | 0 | YES |  |  |  |  | Yes | 1 | Conceptual
306655,309275,1 | 306655 | SALISBRY | 309275 | NORAND BL | 1 | 100 | Line | COLLINS BL | 100 kV Line | 101.8 | 0 | 0 | 0 | 0 | 101.7 | 158.9 | 189.9 | 156.6 | 168.7 | 203.8 | 176.9 | 187.9 | 163.8 | 186.4 | 0 | 0 | 0 | 0 | 100.7 | 123.4 | 99 | 106.1 | 111.9 | 112.3 | 102.5 | 113.8 | 203.8 | 3 | 7 | YES |  |  |  | 1472 | Yes | 3 | No
309275,309276,1 | 309275 | NORAND BL | 309276 | SWINK BL | 1 | 100 | Line | COLLINS BL | 100 kV Line | 99.4 | 0 | 0 | 0 | 0 | 99.4 | 156.4 | 187.1 | 154.3 | 166.1 | 201.3 | 174.1 | 184.9 | 161.4 | 183.4 | 0 | 0 | 0 | 0 | 99.2 | 121.9 | 97.5 | 104.5 | 110.3 | 110.7 | 101.1 | 112.2 | 201.3 | 2 | 4 | YES |  |  |  | 1472 | Yes | 3 | No
306566,309276,1 | 306566 | CHINA GR | 309276 | SWINK BL | 1 | 100 | Line | COLLINS BL | 100 kV Line | [5 empty] | 0 | 152.3 | 165.9 | 149.8 | 156.4 | 181.8 | 166.5 | 169.7 | 151 | 167.7 |  |  |  |  | 0 | 106.9 | 0 | 99.1 | 99.3 | 95.2 | 0 | 93 | 181.8 | 2 | 3 | YES |  |  |  | 1472 | Yes | 3 | No
306566,306671,1 | 306566 | CHINA GR | 306671 | SWINK T | 1 | 100 | Line | COLLINS WH | 100 kV Line | [5 empty] | 0 | 118.9 | 142.4 | 122.2 | 127.5 | 168 | 134.5 | 139.2 | 128.7 | 141.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1 | 168 | 2 | 3 | YES |  |  |  | 2919.8 | Yes | 4 | No
306650,306655,1 | 306650 | NORAND T | 306655 | SALISBRY | 1 | 100 | Line | COLLINS WH | 100 kV Line | 114.6 | 96.4 | 110.4 | 0 | 0 | 114.6 | 181.1 | 215.5 | 176.4 | 191.5 | 223.8 | 200.2 | 214.5 | 183.8 | 210.7 | 0 | 0 | 0 | 0 | 111.4 | 134.6 | 108.8 | 116.8 | 116.2 | 117.3 | 105.2 | 118.1 | 223.8 | 3 | 7 | YES |  |  |  | 1521.8 | Yes | 3 | No
306528,306650,1 | 306528 | JULIANT | 306650 | NORAND T | 1 | 100 | Line | COLLINS WH | 100 kV Line | 111.8 | 0 | 106.8 | 0 | 0 | 111.8 | 178.4 | 212.5 | 173.8 | 188.7 | 221.2 | 197.3 | 211.3 | 181.2 | 207.6 | 0 | 0 | 0 | 0 | 109.8 | 133.1 | 107.3 | 115.2 | 114.6 | 115.7 | 103.7 | 116.5 | 221.2 | 3 | 7 | YES |  |  |  | 1450 | Yes | 3 | No
306528,306671,1 | 306528 | JULIANT | 306671 | SWINK T | 1 | 100 | Line | COLLINS WH | 100 kV Line | [5 empty] | 0 | 140.6 | 169.3 | 140.2 | 150 | 187 | 157.9 | 167.1 | 147.1 | 166.6 |  |  |  |  | 0 | 113.7 | 0 | 96.7 | 96.3 | 96 | 0 | 98.2 | 187 | 2 | 3 | YES |  |  |  | 1450 | Yes | 3 | No
306573,309611,1 | 306573 | CONCORD | 309611 | CONCORD4 | 1 | 100 | Line | CONCORD BL | 100 kV Line | 0 | 109.5 | 124.9 | 95.1 | 110.4 | 0 | 110.2 | 125.5 | 95.5 | 110.2 | 95.8 | 110.7 | 125.7 | 95.7 | 110.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.7 | 3 | 3 | YES | 158.3 |  |  |  | Yes | 2 | Conceptual
306641,309297,1 | 306641 | POPLAR S | 309297 | MAJOLICA BL | 1 | 100 | Line | GRANTS CREEK BL | 100 kV Line | [10 empty] | 107 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 107 | 1 | 1 | NO |  |  |  |  | No | 0 | No
306616,306641,1 | 306616 | MAJOLICA | 306641 | POPLAR S | 1 | 100 | Line | GRANTS CREEK WH | 100 kV Line | [10 empty] | 116.6 | 95.9 | 95.8 | 90.6 | 96.3 | [8 empty] | 0 | 91 | 0 | 0 | 116.6 | 1 | 1 | NO |  |  |  | 1496 | Yes | 2 | No
306560,306655,2 | 306560 | BUCK S34 | 306655 | SALISBRY | 2 | 100 | Line | SALISBURY BL | 100 kV Line | 112 | 97.8 | 115.8 | 0 | 0 | 112 | 167 | 198.4 | 160.5 | 175.8 | 203.4 | 183.2 | 197.9 | 166.6 | 192.2 | 0 | 0 | 0 | 0 | 102.8 | 123 | 99.3 | 107.3 | 108.4 | 110.7 | 98.1 | 109.9 | 203.4 | 3 | 7 | YES |  |  |  | 1595.5 | Yes | 3 | No
306560,306655,1 | 306560 | BUCK S34 | 306655 | SALISBRY | 1 | 100 | Line | SALISBURY WH | 100 kV Line | 112 | 97.8 | 115.8 | 0 | 0 | 112 | 167 | 198.4 | 160.5 | 175.8 | 209.7 | 183.2 | 197.9 | 166.6 | 192.2 | 0 | 0 | 0 | 0 | 102.8 | 123 | 99.3 | 107.3 | 108.4 | 110.7 | 98.1 | 109.9 | 209.7 | 3 | 7 | YES |  |  |  | 1595.5 | Yes | 3 | No
306629,306681,1 | 306629 | MORESVIL | 306681 | WESTFORK | 1 | 100 | Line | SHERRILL BL | 100 kV Line | 0 | 0 | 108.1 | 0 | 0 | 119.6 | 0 | 106 | 0 | 0 | 120.7 | 92.9 | 107.4 | 0 | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7 | 3 | 2 | YES | 125.6 |  |  |  | Yes | 2 | TBD
306629,306681,2 | 306629 | MORESVIL | 306681 | WESTFORK | 2 | 100 | Line | SHERRILL WH | 100 kV Line | 0 | 0 | 108.1 | 0 | 0 | 119.9 | 0 | 106 | 0 | 0 | 120.9 | 92.9 | 107.4 | 0 | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.9 | 3 | 2 | YES | 126 |  |  |  | Yes | 2 | TBD
306687,308871,1 | 306687 | WINECOFF | 308871 | POPLRT B | 1 | 100 | Line | SKYBROOK BL | 100 kV Line | 105.9 | 102.8 | 119.3 | 0 | 98.5 | 105.9 | 118.3 | 137.2 | 108 | 122.6 | 133.9 | 127.5 | 142.3 | 113.2 | 135.5 | 0 | 0 | 0 | 0 | 0 | 95.1 | 0 | 0 | 90.8 | 90.1 | 0 | 92.3 | 142.3 | 3 | 6 | YES |  |  | 116 | 220 | Yes | 3 | Conceptual
308259,308871,1 | 308259 | EASTFLDR | 308871 | POPLRT B | 1 | 100 | Line | SKYBROOK BL | 100 kV Line | 0 | 0 | 95.8 | 0 | 0 | 0 | 100.8 | 112.3 | 0 | 104.3 | 117.1 | 109 | 115 | 95.9 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.1 | 2 | 3 | YES |  |  |  | 160 | Yes | 2 | Conceptual
306642,306687,1 | 306642 | POPLR TN | 306687 | WINECOFF | 1 | 100 | Line | SKYBROOK WH | 100 kV Line | 95.6 | 0 | 106.1 | 0 | 0 | 95.6 | 106.1 | 122.5 | 98.9 | 113.7 | 122 | 114.3 | 125.4 | 101.2 | 119.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.4 | 3 | 3 | YES |  |  | 104.9 | 220 | Yes | 3 | Conceptual
Note on AT5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?